Appendix

for

Impact and Persistence Evaluation Study of Connecticut Light and Power’s Operation and Maintenance Services Program (2002 - 2004)

Appendix 1: Comprehensive Project List	2

Appendix 2: Measurement and Verification Plan	5

Appendix 3: Project Summary Information	13

Appendix 4: Survey Instrument	176

# Appendix 1: Comprehensive Project List

The following table, which is based on an extract of NU’s program tracking database, lists each project in CL&P’s O&M Services Program along with savings values from CL&P’s database (annual kWh, lifetime kWh, and kW) and an indication if Nexant sampled and inspected the project.

| Project No. | CL&P Annual kWh Savings | CL&P Lifetime kWh Savings | CL&P kW savings | Nexant Sample | Nexant Inspected |
| --- | --- | --- | --- | --- | --- |
| CE02M007 | 290,272 | 1,131,075 |  | Yes | No |
| CE03M002 | 201,376 | 1,712,370 |  | Yes | Yes |
| WE04M010 | 171,696 | 349,810 |  | Yes | No |
| CE04M007 | 567,920 | 513,545 | 9.4 | Yes | No |
| WE04M018 | 250,441 | 2,547,976 |  | Yes | Yes |
| CE02M005 | 737,568 | 0 | 0 | Yes | Yes |
| WE03M005 | 171,237 | 2,575,440 |  | Yes | Yes |
| WE02M003 | 118,145 | 1,081,440 | 0 | Yes | Yes |
| CE04M008 | 159,249 | 1,117,980 |  | Yes | Yes |
| EA01M013 | 371,342 | 356,840 | 2.6 | Yes | Yes |
| WE01M038 | 214,463 | 3,845,640 |  | Yes | No |
| EA01M017 | 238,272 | 2,982,780 |  | Yes | No |
| WE01M040 | 148,636 | 2,752,425 |  | Yes | No |
| EA00M011 | 127,580 | 3,045,055 |  | Yes | No |
| WE04M013 | 183,495 | 951,490 |  | Yes | Yes |
| EA01M004 | 114,583 | 1,443,780 | 0 | Yes | Yes |
| CE02M003 | 344,800 | 4,774,855 |  | Yes | No |
| CE02M006 | 273,145 | 65,844 |  | Yes | Yes |
| CE04M001 | 263,412 | 6,164,400 |  | Yes | Yes |
| WE04M002 | 264,858 | 2,979,120 |  | Yes | No |
| CE04M006 | 198,608 | 2,648,580 |  | Yes | Yes |
| WE02M014 | 105,583 | 922,270 | 0 | Yes | Yes |
| CE02M002 | 365,537 | 692,440 |  | Yes | Yes |
| EA04M002 | 384,564 | 241,500 | 0 | Yes | Yes |
| CE01M007 | 126,501 | 0 | 0 | Yes | Yes |
| CE04M003 | 370,816 | 2,634,120 |  | Yes | Yes |
| WE01M027 | 0 | 159,075 | 0 | Yes | Yes |
| EA01M010 | 0 | 323,385 | 0 | Yes | Yes |
| CE01M026 | 6,056 | 0 | 0 | Yes | No |
| EA02M007 | 45,406 | 1,438,875 | 0 | Yes | Yes |
| WE02M004 | 85,010 | 0 | 0 | Yes | Yes |
| CE04M004 | 91,657 | 0 | 0 | Yes | Yes |
| CE01M028 | 0 | 134,140 | 0 | Yes | No |
| WE01M034 | 0 | 3,216,945 | 0 | Yes | Yes |
| WE02M009 | 21,559 | 35,740 | 0 | Yes | Yes |
| WE02M011 | 65,157 | 340,990 | 0 | Yes | Yes |
| CE01M018 | 0 | 424,160 | 0 | Yes | Yes |
| EA02M010 | 94,760 | 0 | 0 | Yes | Yes |
| EA01M009 | 0 | 90,315 | 0 | Yes | Yes |
| EA03M001 | 42,661 | 0 | 0 | Yes | Yes |
| WE01M019 | 0 | 384,380 | 0 | Yes | Yes |
| WE01M032 | 0 | 473,800 | 0 | Yes | Yes |
| WE02M016 | 10,500 | 0 | 0 | Yes | Yes |
| EA00M020 | 49,061 | 459,070 | 0 | Yes | Yes |
| EA01M012 | 0 | 758,700 | 0 | Yes | Yes |
| WE02M002 | 26,828 | 507,785 | 0 | No | NA |
| CE01M017 | 0 | 761,180 | 0 | No | NA |
| WE01M036 | 96,444 | 0 | 0 | No | NA |
| EA01M011 | 0 | 554,460 | 0 | No | NA |
| CE01M016 | 0 | 656,640 | 0 | No | NA |
| WE02M003 | 0 | 0 | 0 | No | NA |
| WE02M008 | 76,228 | 4,479,125 | 0 | No | NA |
| CE01M002 | 89,730 | 30,280 | 0 | No | NA |
| WE04M004 | 79,730 | 0 | 0 | No | NA |
| EA01M003 | 91,814 | 0 | 0 | No | NA |
| WE02M013 | 50,580 | 490,610 | 0 | No | NA |
| WE01M033 | 0 | 639,915 | 0 | No | NA |
| CE01M031 | 39,999 | 0 | 0 | No | NA |
| CE01M019 | 0 | 454,315 | 0 | No | NA |
| CE04M005 | 16,461 | 0 | 0 | No | NA |
| WE04M011 | 74,532 | 1,724,000 | 0 | No | NA |
| CE02M009 | 38,438 | 0 | 0 | No | NA |
| WE04M006 | 34,981 | 0 | 0 | No | NA |
| EA02M009 | 13,889 | 0 | 0 | No | NA |
| EA02M099 | 7,148 | 0 | 0 | No | NA |
| CE01M030 | 0 | 2,717,335 | 0 | No | NA |
| CE04M002 | 34,622 | 1,856,710 | 0 | No | NA |
| EA02M001 | 101,557 | 0 | 0 | No | NA |
| EA02M005 | 31,815 | 1,191,360 | 0 | No | NA |
| WE03M001 | 17,842 | 0 | 0 | No | NA |
| CE01M012 | 66,046 | 11,063,520 | 0 | No | NA |
| WE02M012 | 90,588 | 0 | 0 | No | NA |
| WE02M001 | 76,790 | 439,690 | 0 | No | NA |
| CE01M021 | 0 | 858,265 | 0 | No | NA |
| CE00M037 | 0 | 0 | 0 | No | NA |
| WE01M041 | 42,416 | 0 | 0 | No | NA |
| WE02M006 | 6,021 | 0 | 0 | No | NA |
| EA01M008 | 0 | 425,050 | 0 | No | NA |
| WE01M020 | 0 | 3,020,640 | 15.4 | No | NA |
| WE01M017 | 0 | 1,055,830 | 0 | No | NA |
| CE01M015 | 0 | 0 | 0 | No | NA |
| WE01M018 | 0 | 2,043,790 | 0 | No | NA |
| WE01M030 | 0 | 90,812 | 0 | No | NA |
| WE01M031 | 0 | 69,445 | 0 | No | NA |
| WE01M042 | 65,467 | 1,511,548 | 0 | No | NA |

# Appendix 2: Measurement and Verification Plan

The M&V plan for O&M Service program is comprised of three individual plans for process, cooling, and refrigeration measures.  In each individual plan, the activities cover the fields as described in Task 5 in Work Plan.

Process Measure M&V Plan

Measure Definition

Process measures typically result in compressor power reduction by reducing compressed airflow rate, compressor operation hours or discharge pressure.  This M&V method is appropriate for the following measures:

- Compressed air leakage repair

- No-loss drain replacement

- Compressor sequencing

- Reduce distribution system pressure

- Install solenoid valves

- Shut off major compressors

- Install blower to reduce compressor load

- Replace air-driven mixer with electricity-driven mixer

Baseline Identification

Baseline operating data cannot be collected at the evaluation stage, so the researcher must rely on the record as found in electronic and paper files, and then supplement this with information obtained during participant interviews while on site.  The major identification should focus on determining compressor energy consumption in the baseline condition.  The interview may include at least:

- Daily, weekly, seasonal and annual operating and production hours; or schedules for each shift if applicable.

- Load characteristics including daily, weekly and seasonal average compressor airflow (CFM) load; or compressor airflow load demand for each shift if applicable.

- Demand (kW).

- Independent variables including actual operating pressure, etc.

- Performance factors:

- Compressor nameplate including at least compressor type, airflow, working pressure, efficiency,

- Compressor control methods;

- Compressor operation data or power percentage versus airflow (CFM) load percentage.

- Compressor power/load data sheet at different compressor discharge pressure if possible.

- Spot metering compressor kW or kW trending data if possible.

Post-installation Inspection or Site Survey

The first focus of post-installation inspection is to verify that all the proposed retrofit measures have been installed and operate as proposed.

- Compressed air leakage repair

  - Verify that claimed leakage has all been repaired.  Since typically there were a number of leakage locations, sampling method can be used for this case.  Samples should be among the large airflow leakage group.  Apply the sampled percentage rate of repair completion to all the claimed air leakages.  Compressed airflow rate reduction should be calculated based on the actual repair completion.

  - Collect the sizes of the typical leakage type

- No-loss drain replacement

  - Verify that all the drains have been replaced

  - Verify the size of each drain

  - Verify new drain discharge performance

- Compressor sequencing

  - Verify compressors are controlled in sequence

  - Collect actual sequencing

- Reduce distribution system pressure

  - Verify actual distribution system pressure value

- Install solenoid valves

  - Verify solenoid valves have been installed

  - Verify the new valves are actually controlled

- Shut off major compressors

  - Verify major compressors are shut off during off peak or off shift period

- Install blower to reduce compressor load

  - The blower has been installed

  - Verify that the blower is being used for the special process when the major production process is off

- Replace air-driven mixer with electricity-driven mixer

  - Verify that the mixture is being driven by electricity

The post-installation may also include:

- Collect daily, weekly, seasonal and annual operating and production hours if operation hours are different from the baseline.

- Load characteristics including daily, weekly and seasonal average compressor airflow (CFM) load if the operation is different from the baseline.

- Post-installation operating pressure.

- New equipment or parts nameplates including type, kW power and efficiency

- Spot metering compressor kW or kW trending data if possible

Compressor Airflow Reduction

Since the reduction of compressed airflow rate is the direct cause of compressor energy savings and crucial for energy savings calculation, it is critical to calculate and estimate compressed air flow in the baseline and post-installation accurately.  The estimation and calculation varies from implemented measures.  The following methods may be used

Compressed Air Pressure Reduction

The airflow can be calculated using the following equations,

Airflow demand reduction CFM = CFMbaseline − CFMpost

Where:

CFMbaseline 	= Airflow demand in the baseline condition

CFMpost 	= Airflow demand in the post-installation

CFMpost can be calculated as

CFMpost = CFMbaseline × (compressed air pressure in the post-installation / compressed air pressure in the base condition)^0.5

Air Leakage Repair

Airflow reduction CFM = Air leakage repair CFM

Air leakage repair CFM can be determined by

- Leakage airflow measurement

- Leakage rates of equivalent orifice at actual pressure and equivalent orifice size

Replace with No-loss Drain

Airflow reduction CFM = Airflow waste CFM by old when no condensation

Airflow deduction CFM can be determined by

Compressed air release CFM = Standard airflow CFM × Coefficient of flow

Equations for Calculating Demand and Energy Savings

- Calculate Kilowatt savings

In general, compressor kW savings is calculated using the following equation

kW savings =

Where:

kWbaseline = 	Kilowatt demand of baseline compressor in particular operating scenario

kWpost = 	Kilowatt demand of post-installation compressor in particular operating scenario

Specifically, kW savings may be calculated using the following options depending on the compressor type and control method or data availability.

Option 1: If the compressor operation data of percentage of full load kW versus percentage of rated airflow rate (CFM) is known, the kW savings can be calculated by the following equation,

kW savings = [Baseline airflow percentage relative to compressor rated airflow (% CFM)] × [Kilowatt percentage relative to full load power at the baseline airflow percentage (% FL kW)] −

[Post installation airflow percentage relative to compressor rated airflow (% CFM)] × [Kilowatt percentage relative to full load power at the post-installation airflow percentage (% FL kW)]

Option 2: If the compressor operation data is not available, kW savings can be estimated by the equation

kW savings = [Compressor airflow demand reduction (CFM)] × [Operating efficiency (kW/CFM)]

Where,

Kilowatt demand per airflow (kW/CFM) depends on the compressor type

kW/CFM =

0.22 to 0.24 	Single acting, air-cooled reciprocating air compressors

0.15 to 0.16 	Double acting, water-cooled reciprocating air compressors

0.18 to 0.19 	Lubricant-injected rotary screw compressors, single-stage

0.16 to 0.17 	Lubricant-injected rotary screw compressors, two-stage

0.18 to 0.22 	Lubricant-free rotary screw compressors

0.16 to 0.20 	Centrifugal air compressors

- Calculate kWh savings

Kilowatt-hour energy is generally calculated by the following equation:

Energy Savings =

Where:

HR = 		Compressor operation hours, hrs

i =		1 to N

N = 		Number of shift or scenario

Compressor operation hours (HR) depending on the compressor control method. It may be determined using the following two options:

Option 1: If the compressor operates continuously, calculate the compressor operation hours (HR) by

HR = 		Production hours

Option 2: If compressors operate at load/No-load method, calculate the compressor operation hours (HR) by the following equations.

HR on load = [Production Hours] × [Ratio of airflow demand at load over the rated compressor airflow rate]

HR on no-load = [Production Hours] × [1 − Ratio of airflow demand at load over the rated compressor airflow rate]

Kilowatt is full load compressor electricity demand in this option.

Cooling Measure M&V Plan

Measure Definition

Cooling related measures typically result in chiller or cooling generation power reduction by reducing electricity demand and equivalent full load hours.  This M&V method is appropriate for the following measures, but not limited to these measures.

- Install VFDs for air handling units

- Repair/replace chilled water valves for air handling units

- Repair/replace terminal mixing boxes

- Clean condensing or evaporator coils

- Repair duct work leakage

- Add set back/set forward for thermostats or air conditioner

- Install/furnish energy management system (EMS)

Baseline Identification

The major baseline identification should focus on determining chiller demand and energy consumption in the baseline condition.  The identification includes data collection and survey interviews covering the following information:

- Facility physical dimensions and features

- Major space functions that the chillers server

- Facility occupancy daily, weekly and seasonal schedules

- Chillers and related air handling equipments operating hours

- Performance factors kW/ton and part load efficiency IPLV

- Chillers and related air handling units control sequences

- Weather data of the site where the facility is located

- Spot metering chillers kW or kW trending data if possible

Post-installation Inspection or Site Survey

The focus of post-installation inspection is to determining chiller demand and energy consumption in the post-installation condition.  The site survey includes:

- Verify that all the measures have been installed and implemented as proposed.

- Verify other renovations that have impact on cooling energy since the baseline conditions, if any.

- Collect daily, weekly, seasonal and annual operating schedules if different from the baseline conditions.

- Collect occupancy condition if it is different from the baseline conditions.

- Conduct spot metering chillers kW or collect kW trending data if possible.

Equations for Calculating Demand and Energy Savings

  - Calculate Kilowatt savings

In general, compressor kW savings is calculated using the following equation

kW savings =

Where:

kWbaseline = 	Kilowatt of cooling equipment in the baseline condition

kWpost = 	Kilowatt of post-installation cooling equipment in the post-installation condition

Kilowatt savings may be calculated by the equation

kW savings =

Reduced cooling load tons × chiller or cooling generating equipment rated kW/ton

  - Calculate Kilowatt-hour savings

Kilowatt-hour energy is generally calculated by the following equation:

Energy Savings =

Where:

HR = 		Chiller operation hours, hours

i =		1 to N

N = 		Number of scenarios

Kilowatt-hour energy may also be estimated by the equation:

Energy Savings = chiller or cooling equipment IPLV × (EFLHbaseline − EFLHpost)

Where:

IPLV = 	Integrated partial load value

EFLHbaseline = 	Full load equivalent hours in the baseline condition, hours

EFLHpost = 	Full load equivalent hours in the post-installation condition, hours

Refrigeration Measure M&V Plan

Measure Definition

Refrigeration measures are typically installed in grocery stores.  The M&V method is appropriate for the following measures:

- Re-commissioning the existing refrigerating system to provide operation at optimum efficiency levels for the current conditions in the facility

- Replace meat room evaporating air units

- Furnish and install insulated door system

- Repair general impact doors in food refrigerating units and systems

- Install high speed door system for cooler room

- Install hot gas by-pass for coils

- Install a monitoring system cable of recording the electricity power and energy usage of the major areas of electricity usage

Baseline Identification

The major identification should focus on determining if the baseline conditions were as stated or assumed.  The interview may include at least:

- Daily, weekly, and annual operating and production hours

- Collect spot metering kW or kW trending data if possible

Post-installation Inspection or Site Survey

The site survey includes:

- Monitoring system

- Verify the proposed monitoring systems have been installed and function as intended

- Clarify specific measures being taken utilizing the monitoring system to reduce energy consumption

- Other measures

- Verify that all the proposed measures have been installed and function as intended

- Collect utility bills of the same seasons or months in the baseline and post installation periods

- Collect spot metering kW or kW trending data if possible

- Daily, weekly, and annual operating and production hours, if the hours are different than the baseline conditions

Equations for Calculating Demand and Energy Savings

- Calculate Kilowatt savings

In general, kW savings is calculated using the following equation

kW savings =

Where:

kWbaseline = 	Kilowatt of cooling equipment in the baseline condition

kWpost = 	Kilowatt of post-installation cooling equipment in the post-installation condition

- Calculate Kilowatt-hour savings

Kilowatt-hour energy is generally calculated by the following equation:

Energy Savings =

Where:

HR = 		Operation hours

i =		1 to N

N = 		Number of scenario

# Appendix 3: Project Summary Information

This appendix provides detailed information on each of the 37 projects analyzed by Nexant. Included are project descriptions, measure descriptions, equipment descriptions, inspection findings, savings calculations, and results.

Nexant’s energy savings (kWh and kW) calculation steps for common compressed air measures among the 37 projects are described below.

kWh Savings

Measure 1:  Repair compressed air leakage.

- Determine reduced air flow rate CFM.

This value is estimated based on documented air leak repair, Nexant’s site inspection check as well as the repair percentage estimated by facility representatives.

- Determine related compressor(s) operating efficiency (kW/cfm).

Option1: the efficiency is estimated based on compressor data (cfm, hp, motor efficiency, discharge air pressure, control method, cooling type) which is collected by site inspection or by contacting manufactures.

Option 2: if there is no compressor data available, use a general efficiency data presented in Improving Compressed Air System Performance-a source book for industry depending on the compressor type

kW/cfm =

0.22 to 0.24 	Single acting, air-cooled reciprocating air compressors

0.15 to 0.16 	Double acting, water-cooled reciprocating air compressors

0.18 to 0.19 	Lubricant-injected rotary screw compressors, single-stage

0.16 to 0.17 	Lubricant-injected rotary screw compressors, two-stage

0.18 to 0.22 	Lubricant-free rotary screw compressors

0.16 to 0.20 	Centrifugal air compressors

- Determine annual operating hours.

This value is determined by site interview with facility representatives.

- Calculate kWh savings.

kWh savings = reduced air flow (cfm) × compressor operating efficiency (kw/cfm) × annual operating hours (hr)

Measure 2: Replace old drains with no-loss drains.

- Collect the following information:

diameter of drains (inch), compressed air pressure (psig), and old drains operating cycle (XX seconds on for every XX seconds).

- Determine standard airflow of each drain based on the principle of orifice (cfm).

Nexant uses the table “Discharge of Air through an Orifice” provided in page 232 of the Compressed Air and Gas Handbook.

- Determine old drain airflow rate (cfm) of each drain.

Old drain air flow = standard airflow rate (cfm) × × coefficient of flow,

where – coefficient of flow is typically no more than 0.65 referring to Compressed Air and Gas Handbook

- Sum airflow rate (cfm) of all replaced old drains.

- Determine compressor operating efficiency (kW/cfm).

Use the same procedure as step (2) for measure 1.

- Calculate kWh savings for all drains.

kWh savings = old drain airflow rate (cfm) × compressor operating efficiency (kW/cfm) × annual operating hours (hr)

Measure 3: Other types of compressed air flow reduction measures.

Measures generally include

- Shut off major compressors

- Install blower to reduce compressor load

- Replace air-driven mixer with electricity-driven mixer

- Install solenoid valves

The general steps for these measures are:

- Determine reduced air flow rate (cfm).

This value is based on interview with facility representatives or replaced machine airflow requirement

- Determine related compressor(s) operating efficiency (kW/cfm).

- Determine new electric machine power consumption (kW) if applicable.

- Determine annual operating hours.

This value is determined by site interview with facility representatives.

- Calculate kWh savings.

kWh savings = (reduced air flow (cfm) × compressor operating efficiency (kw/cfm) – new electric machine power (kW) if applicable) × annual operating hours (hr)

kW Savings:

- For the measures related to reducing compressed airflow, such as compressed air leakage repair and no-loss drain replacement, Nexant’ demand savings is 0 kW provided that the related compressors control method is load/no load.

- All measures with only impact on night shifts have no demand savings in this study.

- Except for the above two conditions, kW savings is generally calculated by

kW savings = reduced air flow (cfm) × compressor operating efficiency (kW/cfm)

Nexant’s energy savings (kWh and kW) calculation methodology for non-compressed air measures including refrigeration, cooling and HVAC measures are summarized in specific projects due to the varieties.

The following general notes apply to all 37 projects in this appendix:

- The “Inspection Action Items” in each project summary lists Nexant’s data collection plan for site inspection.  The “Inspection Findings” in each project summary as well as the related equipment information document the findings Nexant was able to obtain from site inspection.  In most cases, many listed plans in the “Inspection Action Items” could not be obtained through site inspection and post-inspection endeavour.  Nexant’s kWh and kW estimation is generally based on available site inspection findings, documented information and compressors reference books.

- For all the measures that could not be located by site interviewers during Nexant’s site inspection, Nexant assumes these measures have been installed and maintained.  This assumption is based on the fact that CL&P has inspected all the measures installed in the CL&P O&M program performed between 2001 and 2005.

- During site inspection, Nexant intent to inspect individual installed measures except for compressed air leak repair.  For this measure, Nexant used the sampling method combined with interview with facility representatives.  Typically, the sample size is 10% to 30% of entire repaired leaks depending on their total numbers.  Leak sample check covers different leak sizes.  General locations of inspected leaks includes valves sealing, flange gaskets, air gun to hose connections, and other sealing and connections.  The results of sampling check and interview have been used to estimate kWh savings for the measure of repairing air leaks.

- For the projects without a Nexant Calculations Summary indicates that no original calculations were found in the documents that CL&P sent to Nexant.

- For the measures that were not implemented according to Nexant’s site inspection, there is no savings in Nexant’s impact analysis.

- For the measures that are documented by “this measure did not work per documentation” but was found actually implemented according to Nexant’s site inspection, Nexant estimates their savings based on site data collection and involves the savings in the impact analysis.

- The “Inspection Action Items” of some projects (especially for HVAC related measures) lists information collection plans for estimating measure savings in different ways in order to prevent unavailability of some information.  For the projects where some data could not be collected, Nexant uses collected information, project documentation and experience to estimate savings.  If no data could be collected, Nexant takes the reported measure savings.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-02-M-005 |
| Building Type | manufacturing |
| Building Square Feet | 168,000 |
| Project Completion Date | 11/22/2002 |
| Annual Energy Savings (kWh) | 737,568.00 |
| Lifetime Energy Savings (kWh) | 11,063,520.00 |
| Total Incentives | $18,160.80 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/21/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1B | 2 |
| --- | --- | --- |
| Measure Description | Furnish and install EMS to control 27 AHUs | (1) Add VFDs to Primer and Finish spray booths fans & make-up air fans; (2) Interlock to guns |
| Measure Life (years) | 15 | 15 |
| Total Number of Units | 109 control points |  |
| CL&P-reported kWh Savings | 737,568.00 |  |
| Assumptions in CL&P-reported Savings | 1) EER = 7.2 2) Pre EFLH =1488 Post EFLH = 589 |  |
| Calculation Methodology for CL&P-reported Savings | 1) Total 27 RTUs cooling demand 820.33kW x (1488-589)EFLH x 0.85? 2) Total 27 RTUs fan demand 129.85kW x (1488-589)EFLH x 0.85? |  |
| Inspection Action Items | 1) Collect name plate for 27 units and fan power information. 2) Check if all 23 AHUs and 4 RTUs has the same EER = 7.2? 3) Measure actual fan power by sampling. 4) What exactly have been implemented? 5) What is night time reset temperatures? 6) What is night time reset enabling hours? 7) What is actual EFLH pre and post EEM1#, 1488 or 589? 8) Building/production occupancy profile? 9) All 27 units serves interior or exterior area? % of footage? 10) Were all 27 units implemented with night time reset? 11) Pick up some AHUs to check the current AHU operation hours; verify the night time set back control? 12) Ask for utility bill pre and post installation if possible? | Ask other measures have been implemented or not? |
| Inspection Findings | 1) The controls were found implemented by inspecting the control system. 2) Per the facility manager and control system schedules, the differences pre and post the program are: Before EEM: - 27 AHUs operated 24/7 - there was no night time space temperature reset After EEM: - Typical AHUs operating hours for 4 office AHUs: M – F: 5:30am to 5:30pm; Saturday – Sunday: Off - Typical AHUs operating hours for 23 factory AHUs: M – F: 6:00am to 3:00pm (overtime 6:00am to 5:30pm) Saturday for 6 of the 23 AHUs : 6:00am to 11:00am Sunday: off - Night time space temperature reset: 4 office AHUs: Unocc. 80F cooling /58F heating. 23 factory AHUs: Unocc. 82F cooling /58F heating. | 1) Per the facility manager, this measure was not implemented |

| Measure # | 3 | 4 |
| --- | --- | --- |
| Measure Description | Add Interlock control to Votex spray booth exhaust fan and make-up air fan | Vent the air-cooled compressor to the outside |
| Measure Life (years) | 15 | 10 |
| Total Number of Units |  |  |
| CL&P-reported kWh Savings |  |  |
| Assumptions in CL&P-reported Savings |  |  |
| Calculation Methodology for CL&P-reported Savings |  |  |
| Inspection Action Items |  |  |
| Inspection Findings | 1) Per the facility manager, this measure was not implemented | 1) Per the facility manager, this measure was not implemented |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1B | Install EMS for 27 Units | 589 |  | 620,890 | 677,390 | 15 | 15 | 9,313,350 | 10,160,844 | 0.00 | 0.00 |
|  |  | 589 |  | 116,678 |  | 15 | 15 | 1,750,170 |  |  |  |
| Project level |  |  |  | 737,568 | 677,390 |  |  | 11,063,520 | 10,160,844 |  |  |

| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 4 office AHUs total fans power 8.7282 kW EER for office AHU= 6 (manufacturer data) | 6 | manufacturer's data |  |
|  | 4 office AHUs total compressor power 90 kW EER for factory AHU= 8.571428571 | 8.571428571 |  |  |  |
|  | 17 factory RTUs total fans power 5.6035 kW |  |  |  |  |  |
|  | 17 factory RTUs total compressor power 476 kW |  |  |  |  |  |
|  | 6 factory RTUs total fans power 30.213 kW |  |  |  |  |  |
|  | 6 factory RTUs total compressor power 150.5 kW |  |  |  |  |  |
| EEM1# | 4 office AHUs scheduled operating hours reduction 5736 hrs | estimated operating hours during the unocc. period: 2,135 hrs |  |
|  | 17 factory AHUs scheduled operating hours reduction 6492 hrs | estimated operating hours during the unocc. period: 2,135 hrs | 2135 |
|  | 6 factory AHUs scheduled operating hours reduction 6232 hrs | estimated operating hours during the unocc. period: 2,348.5 hrs | 2348.5 |
|  | Estimated operating hours for 4 office AHUs during the unocc. Period 2135 hrs |
|  | Estimated operating hours for 17 factory AHUs during the unocc. Period 2135 hrs |
|  | Estimated operating hours for 17 factory AHUs during the unocc. Period 2348.5 hrs |
|  | Fan power savings during unoccupied periods when the outside air temperature between 50F and 72F = = 284,179 kWh |
|  | Estimated operating hours during the unocc. Period when the outside air temperature is between 72 and 82F is 656 hrs |
|  | Estimated cooling capacity when the outside air temperature is between 72F and 82F is 40% |
|  | Cooling savings due to night time reset when the outside air temperature is between 72F and 82F |
|  | = = 269,711 kWh |  |  |  |  |
|  | Estimated operating hours during the unocc. period when the outside air temperature is higher than 82F is 180 hrs. |
|  | Factory part of this facility has total envelope size: 553.3’ by 281.3’ |
|  | Office part of this facility has total envelope size: 254.3’ by 153.6’ |
|  | Total ton-hours savings for the factory part: 27106.7 |  |
|  | Total ton-hours savings for the factory part: 7694.8 |  |
|  | Total kWh savings for the office part = total ton-hrs for the office part / (12/EER) = 15,390 kWh |  |
|  | Total kWh savings for the office part = total ton-hrs for the factory part / (12/EER) = 37,949 kWh |  |  |  |  |
|  | Electricity savings due to the night time reset = 15,390 + 37,949 = 53,339 kWh |  |  |  |  |
|  | Estimated operating hours when the outside air temperature is lower than 50F for the office 3045 hrs |  |  |  |  |
|  | Estimated operating hours when the outside air temperature is lower than 50F for the office 2289 hrs |  |  |  |  |
|  | Assume 75% of AHUs runs |  |
|  | Fan power savings due to night time reset when the outside air temperature is lower than 50F |  |  |  |  |  |
|  | = = 70,160 kWh |  |  |  |  |  |
| Total Nexant project adjusted savings = 284,179 + 269,711 + 53,339 + 70,160 = 677,390 kWh/year |  |  | kWh life time |  |

Nexant Calculations Summary: project kWh savings is reduced from 737,568 kWh to 677,390 kWh because

    - Nexant uses different temperature reset schedules for different RTUs and AHUs collected from the facility EMS system while the project document used the same schedules (EFLH) for all 27 units.

    - Nexant conducts more detailed facility load analysis for different units based on collected facility physical dimensions, weather bin data, and temperature set points while the project document used EFLH for all 27 units.

    - Nexant uses different EERs for different units by contacting manufacture while the project document used the same EER for all 27 units.

Related Equipment Information

|  |  | Measure 1 |  |  |
| --- | --- | --- | --- | --- |
|  | Lennox RTU | Lennox RTU | Lennox Multizone | Lennox Multizone |
| Quantity | 22 | 1 | 2 | 2 |
| Manufacturer | Lennox | Lennox | Lennox | Lennox |
| Type | RTU | RTU | Multizone AHU | Multizone AHU |
| Cooling type |  |  |  |  |
| Model | GCS3-2753 | GCS11-953 | DMS-4-185 | DMS-3-360 |
| Tonnage (ton) | 20 | 7.5 | 7.5 | 15 |
| Fan HP (Supply& Return?) | 7.5 | 7.5 | 1.5 | 5 |
| Condenser fan | 1 | 0.33 |  |  |
| CFM rating |  |  |  |  |
| Volt/Amp rating |  |  |  |  |
| Energy rate (Eff.) kW/ton |  |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-04-M-002/01 |
| Facility Type | Manufacturing |
| Building Square Feet | 122,000 |
| Project Completion Date | 12/19/2004 |
| CL&P Annual Energy Savings (kWh) | 384,564.00 |
| CL&P Lifetime Energy Savings (kWh) | 3,845,640.00 |
| Total Incentives | $15,216 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/3/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Repair compressed air leaks |
| Measure Life (years) | 10 |
| Total Number of Units | 307 |
| CL&P-reported annual kWh Savings | 384,564.00 |
| Assumptions in CL&P-reported Savings | (1) Leakage: Main Area 179 leaks 132cfm Middle Area 80 leaks 38 cfm Black Area 48 leaks 39 cfm Total leakage = 209 CFM (2) Constant compressor efficiency: 0.21kW/CFM |
| Calculation Methodology for CL&P-reported Savings | Demand kW savings = 209 cfm x 0.21 kW/cfm = 43.9 kW Annual kWh savings = 43.9kW x 8760 Hrs = 384564kWh |
| Inspection Action Items | 1) Were all 307 leaks (209cfm) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual production CFM load requirement in the three areas? 5) Verify actual hours (8760)? 6) Collect complete compressors nameplates operation data sheet including power consumption at different CFM? (How kW/cfm change with load for VFD compressor; What power for Full load/no load for base compressor?) If not available, ask control methods for all 4 compressors. 8) What is actual compressor operation pressure? 9) Check service area of the two compressors, Main/Middle/Black. 10) Draw the schematic of production plant (How 4 compressors installed). |
| Inspection Findings | 1) According to the facility representative, this measure have been fully implemented and checked one by one after the implementation. 2) Sample check found no leakage. 3) According to the facility representative, currently, - Sullair compressor, 68hp Atlas and 40 hp Atlas compressor are looped to provide air to the entire production lines; 60 Atlas is dedicated to filter testing in Black Magic department. - Loop operating sequence: primary: Sullair; second: 68 Atlas; third: 40 Atlas - Pressure set points: Loop tank: 110psig; Equipments requirement: 90psig Sullair feeding: 156psig; testing requirement: 125psig. - Right after this measure, 40hp compressor as always off. But it is used now due to enlarged production. - When only Black Magic department is in production, the Sullair compressor runs, and the 68hp compressor VFD is typically in idled mode. 4) Site Observations: - Sullair, 68hp and 60 hp Atlas and Joy compressors were running; 40 Atlas was off. - Sullair compressor operating cycles: 2minutes 3 seconds loaded; 53 seconds unloaded. - Sullair compressor tank pressure reading: 140 psig. - 68hp Atlas compressor 3200-3456 rpm; 113psig - 68hp compressor tank pressure: 110psig. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 8,760 | 8,396 | 384,564 | 339,874 | 10 | 10 | 3,845,640 | 3,398,742 | 43.90 | 5.22 |
| Project level |  |  |  | 384,564 | 339,874 |  |  | 3,845,640 | 3,398,742 |  | 5.22 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1# | Black Magic department annual hours: | 8396 | hrs |  |  |  |  |  |  |
|  | Other production annual hours: |  | 7020 | hrs |  |  |  |  |  |  |
|  | 60hp compressor enabling hours |  | 6257 | hrs |  |  |  |  |  |  |
|  | Sullair, 68 hp and 40hp Atlas compressors enabling hours | 8396 | hrs |  |  |  |  |  |  |
|  | Assume total air leakage | 209 | cfm |  |  |  |  |  |  |  |
|  | 68hp compressor efficiency | 0.201 | kW/cfm |  |  |  |  |  |  |  |
|  | 75hp compressor efficiency | 0.190 | kW/cfm |  |  |  |  |  |  |  |
|  | estimated average compressed air efficiency | 0.194 | kW/cfm |  |  |  |  |  |  |  |
|  | 68hp compressor site speed | 3300 | rpm |  |  |  |  |  |  |  |
|  | maximum |  | 4200 | rpm |  |  |  |  |  |  |  |

Nexant Calculations Summary: project kWh savings reduced from 384,564 kWh to 339,874 kWh because of

- Lower annual operating hours

- Higher compressor power operating efficiency determined by collected individual compressor data through Nexant’s site inspection

Related Equipment Information

|  | Measure 1 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Existing Equipment |  |  |  |  |
|  | Compressor 1 | Compressor 2 (Trim unit) | Compressor 3 | Compressor 4 | Compressor 5 |
| Quantity | 1 | 1 | 1 | 1 | 1 |
| Manufacturer | Atlas Copco | Atlas Copco | Atlas Copco | Joy | Sullair |
| Type | Screw | Screw | Screw |  | Screw |
| Cooling type | Air cooled | Air cooled | Air cooled | Air cooled | Air cooled |
| Model/Ser. | GA30/AII 363698H | GA50 VSDFF/AII 352109H | GA45 |  | 16BS-75H ACAC/603-94245 |
| HP | 60 (motor was remodeled) | 68 | 40 | 20 | 75 |
| CFM rating |  | 324 | 184 |  |  |
| Serving | Dedicated to Black Magic department for filter testing which requires 125 psig. | Main and middle area |  | not for production machines not involved in this measure |  |
| Pressure (PSIG) | Name plate: 183 (tank pressure set at 156psig) | Nameplate: 188 | 150 | 100 (deliver 15-20 psig) | 115/125 |
| Fan motor HP (if air cooled) |  |  |  |  |  |
| Maximum rpm |  | 4820 |  |  |  |
| Dryer information |  |  |  |  | 3ton; 2 hp; 400scfm |
| Control type | Full load/No load | VFD | start/stop; Load/no load |  | Load/no load |
| Motor Eff. |  |  |  |  |  |
| Energy rate (kW/cfm) |  |  |  |  |  |
| Operating Schedule | 24/5 (Monday-Friday) | Secondary | Third |  | Leading (Primary) compressor |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-01-M-013 |
| Facility Type | Manufacturing |
| Building Square Feet | 250,000 |
| Project Completion Date | 12/26/2001 |
| CL&P Annual Energy Savings (kWh) | 371,342.00 |
| CL&P Lifetime Energy Savings (kWh) | 1,856,710.00 |
| Total Incentives | $12,169 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 5/25/2006 |
| Inspected By: | Dakers Gowans and Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on this project documents Nexant received from CL&P |

| Measure # | 1 |
| --- | --- |
| Measure Description | Repair compressed air leaks |
| Measure Life (years) | 5 |
| Total Number of Units | 146 |
| CL&P-reported annual kWh Savings | 371,342.00 |
| Assumptions in CL&P-reported Savings | (1) leakage = 180.5 CFM (2) Annual operation hours: 8000 hours (3) Averaged Trim Unit (Joy) air load is 62.5% (varying between 50% to 75% air load) with 85% of the compressors total connected brake horsepower. (4) Mechanical efficiency = 0.90. |
| Calculation Methodology for CL&P-reported Savings | BASE LINE energy consumption for Trim Unit (Joy): Compressor: 66 BHP/0.90 x 85% x 0.746 x 8000 hrs EEM 1# = 0 kWh savings = Base line - EEM 1# |
| Inspection Action Items | 1) Were all (180.5 CFM) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load profile in the typical daily production? 5) Verify actual hours (8000)? 6) Check that the Trim Unit is actually off in the production? 7) Collect complete compressors (Joy and Quincy) operation data sheet including power consumption at different CFM? 8) What is actual compressor operation pressure? 9) Check or ask how the Quincy compressor changed before and after EEM? |
| Inspection Findings | 1) Two old compressors have been replaced by two new compressors. 2) The two compressors operating 70% and 52% of capacity and 100psig during the site inspection. 3) Sample check of leakage check found no air leakage. 4) Annual operation hours are 7,800. |

| Measure | Measure | Annual Electricity Savings | Lifetime Electricity Savings | Demand Savings |
| --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
|  |  | Annual Cal. (hrs) | Savings (kWh) | Annual Cal. (hrs) | Savings (kWh) | Lifetime (yrs) | Savings (kWh) | Lifetime (yrs) | Savings (kWh) | Savings (kW) | Savings (kW) |
| 1 | Repair Compressed Air Leaks | 8,000 | 371,342 | 7,800 | 228,080 | 5 | 1,856,710 | 5 | 1,140,399 | 2.60 | 14.62 |
| Project level |  |  | 371,342 |  | 228,080 |  | 1,856,710 |  | 1,140,399 |  | 14.62 |
| Nexant Calculation Summary: |  |  |  |  |  |  |  |  |  |
| EEM1# | Assume: |  |  |  |  |  |  |  |  |  |
|  | compressed air repaired | 90% |  |  |  |  |  |  |  |  |
|  | Compressor operating efficiency | 0.18 | kw/cfm |  |  |  |  |  |  |  |
|  | Total leakage | 180.5 | cfm |  |  |  |  |  |  |  |

Nexant Calculations Summary:  project savings reduced from 371,342 kWh to 228,080 kWh because

- Nexant uses lower annual operating hours

- Nexant assumes 90% air leakage repaired reported by the facility representative

- Nexant uses the new compressor power operating efficiency which is higher than in the project document.

| Measure 1 Existing Equipments (replaced by ) 2 new compressors Compressor 1 Compressor 2 (Trim unit) Quantity 1 1 Manufacturer Quincy Joy Type Rotary Screw Rotary Screw Cooling type Air cooled Model QSI 490 TA0265 HP/BHP 100 75/66 CFM rating 490 265 Pressure (PSIG) 100 100 Fan motor HP (if air cooled) Control type Motor Eff. Energy rate (kW/cfm) Operating Schedule | Measure 1 New Equipment Compressors Quantity 2 Manufacturer Ingersoll-Rand Type Cooling type Model N100W/C HP/BHP 100 CFM rating Pressure (PSIG) Max. 145psi Fan motor HP (if air cooled) Control type Motor Eff. Energy rate (kW/cfm) Operating Schedule |
| --- | --- |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-003 |
| Building Type | Hospital |
| Building Square Feet | 689,000 |
| Project Completion Date | 6/10/2005 |
| CL&P Annual Energy Savings (kWh) | 370,816.00 |
| CL&P Lifetime Energy Savings (kWh) | 4,774,855.00 |
| Total Incentives | $82,172.50 |
| Nexant Reviewer | Yujie Cui |
| Inspection Date: | 8/24/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Replace/repair steam and chilled water valves | Repair dual duct CV mixing box pneumatics and calibrate AHU sensors; Shut off units when not used. | Clean AHU evaporator coils and fans and add pleated sealed filters |
| Measure Life (years) | 15 | 15 | 5 |
| Total Number of Units | 29 AHUs | 29 AHUs | 30 AHUs |
| CL&P-reported kWh Savings | 187,830.00 | 94,704.00 | 69,195.00 |
| Assumptions in CL&P-reported Savings | 1) The listed replaced/repaired steam valves and preheat coils have all been repaired. 2) EFLH = 1497; 3) kW/ton = 0.65; 4) del T = 10 F; 5) Saving/F = 0.012; 6) AHU load estimation: 200cfm/ton or 350cfm/ton | 1) The listed DD CV boxes have all been repaired. 2) The listed sensors have all be been calibrated. 3) EFLH = 1497; 4) kW/ton = 0.65; 5) DDBox Save = 0.1 6) Calibrate savings = 0.01 | 1) The listed AHU evaporator coils and fans have all been cleaned. 2) The filters have been added. 3) EFLH = 1497; 4) kW/ton = 0.65; 5) Clean Evp = 0.025 6) Clean Fan = 0.025 |
| Calculation Methodology for CL&P-reported Savings | kW savings: = each AHU estimated tons x 0.65 x 10F x 0.012 kWh savings = EFLH x kW savings | Fixing Boxes kW savings: = each AHU estimated tons x 0.65 x 0.1 kWh savings = EFLH x kW savings Calibrating AHU sensors kW savings: = each AHU estimated tons x 0.65 x 0.01 kWh savings = EFLH x kW savings | Clean Evaporator kW savings: = each AHU estimated tons x 0.65 x 0.025 kWh savings = EFLH x kW savings Clean sensors kW savings: = each AHU estimated tons x 0.65 x 0.025 kWh savings = EFLH x kW savings |
| Inspection Action Items | 1) Collect this building geometry dimensions and envelope information. 2) Ask if all the marked valves and coils in the list have been repaired. 3) Check one or two steam valve samples to test its leakage (measure heating coil discharge air temperatures). 4) Collect chillers system capacity and pumps information (CV?). 5) Collect boilers system capacity and pumps information (CV?). 6) Ask how serious the valves leakages? 7) Ask facility operator if there are regional hot complains before the repairing. 8) Collect chillers operation manual record for 2005 and 2004 in July, August and Sep or more. | 1) Ask if all the listed DD CV boxes have been repaired. 2) Ask if all the listed AHU sensors have been repaired. 3) Ask if all the listed AHUs unocc. shut-off. If not, collect AHUs with shut-off schedules. 4) Sample some AHUs to check their schedules in DDC (if possible print list). 5) Ask how DD CV boxes were fixed? | 1) Ask if all the listed AHU evaporator coils and fans have been cleaned. 2) Sample some coils to check. 3) Check and sample if the filters been added or replaced? 4) Collect all related fan powers. |
| Inspection Findings | 1) According to the contractor, -- the typical steam valve problem was that the valve had been worn out and had serious steam leakage. The typical chilled water valve problem was due to the bad valve pilot positioned. The supply air temperature went down to 45Ｆinstead of 55Ｆfor some AHUs． -- The contractor replaced steam valves and repair or calibrate chilled water valves. -- The following steam & chilled water valves have been repaired: A1 to A12, A14 to A20, A22, A24 to A 31, AS-1, S-1, HV-2, AC-1 to AC-6 -- The following preheat AHUs were replaced: A-1, A-3 and A-6 2) The valves were found replaced or repaired by sampling. | 1) According to the contractor, -- the typical problems with DD CV boxes were that the box actuators were stuck. -- The boxes for the following AHUs have been repaired: A-4 to A-6, A-8 to A-14, A-22, A-29 to A-31, AS-1, -- The sensors for the following AHUs have been repaired: all AHUs except Trane RTU, A-21, A-23, -- The following AHUs were able to be shut off when not needed: A-1to A-2, Trane RTU, A-6 to A-7, A-11, A-14 to A-21, A-24, A-30 to A-31, HV-4, HV-5, S-1, AC-1 to AC-5. -- Currently, AC-1 and AC-4 have schedules 7:00am to 5:00pm. 2) The estimated total tonnage of repaired AHUs was 600 tons. 3) The estimated total airflow rate 180,000 cfm. | 1) According to the contractor, -- The coils for the following AHUs have been cleaned: all AHUs except for A-3 and A-23. -- The fans for the following AHUs have been cleaned. all AHUs except for A-3 and A-23. |

| Measure # | 4 | 5A | 5B (needs to be checked) |
| --- | --- | --- | --- |
| Measure Description | Repair duct work air leaks | Add/repair VFDs control to replace VIV on AC-1,2,3,4 & 5 | Add setback/set forward control for AC-1 and 4 |
| Measure Life (years) | 10 | 15 | 15 |
| Total Number of Units | 24 AHUs |  |  |
| CL&P-reported kWh Savings | 19,087.00 | 101,090.00 | 36,314.00 |
| Assumptions in CL&P-reported Savings | 1) The listed duct work leakage has all been fixed. 2) EFLH = 1497; 3) kW/ton = 0.65; 4) Clean Evp = 0.015 | 1) Minimum terminal box airflow 50%. 2) AC1 to 5 serves exterior zones. 3) VFD fan power use fan affinity law. 4) Savings only happen in Occ. Mode (AHU off during unocc. mode) 5) Occupancy hours = 5836 | 1) AC 2, 3, 4 operation hours was set to: 75hrs/week; Original 24/7 2) No fan power savings. 3) Total peak Tonnage: 81.5ton 4) Peak chiller rate: 0.573kw/ton 5) EFLH: Existing = 1492; proposed= 714 |
| Calculation Methodology for CL&P-reported Savings | kW savings: = each AHU estimated tons x 0.65 x 0.015 kWh savings = EFLH x kW savings | kW savings: (1) 5F Bin (2) for each Bin: Fan power demand: VIV = Tabled VFD = Tabled Fan power savings: (VIV power - VFD power) x occupied hours | Savings: 0.573kW/ton x 81.5 tons x (1492 - 714)hrs = 36314 kWh |
| Inspection Action Items | 1) Ask if all the listed AHU evaporator coils and fans have been cleaned. 2) Ask where did the leakage happen? | 1) Check that VFDs have been replaced/installed for AC 1-5. 2) Check or ask minimum airflow set point 3) Verify serving zone for each AHU. % exterior zones? 4) Check AC 1-5 operation hours. 5) Check Static pressure or terminal box damper positions? (on comp. if it is DDC) 6) Sample VFD speed and power at site visit. | 1) Check which units have set up the setback schedules? 2) Verify that AC2, 3, 4 operation hours has been changed to 75hrs/week. What are the actual schedules? 2) Ask how is the morning warm up is controlled? |
| Inspection Findings | 1) According to the contractor, -- The duct work for the following AHUs have been repaired: all AHUs except for A-16 to A-21 and Trane RTU. 2) On site observation found that the leaked ductwork in the main AHU supply air duct has been fixed using the duct work tape. | 1) According to the contractor, -- Supply and return fans of AC-1 to AC-5 have been replaced with VFDs from the Inlet Guide Vanes. -- VAV terminal box minimum setting is 10% to 30％based on the contractor. 2）The site observation found - All the fans for the 5 AHUs have been installed with VFDs. - The total fan power of these 5 AHUs were found to be 84.5hp. - Fan speeds for AC1 and AC5 were found to be 80% to 100% when the outside air temperature was about 80F during the site visit. | 1) This measure has been included in EEM 2#. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Replace/repair steam and chilled water valves |  |  | 187,830 | 87,360 | 15 | 15 | 2,817,450 | 1,310,400 | 125.50 | 70 |
| 2 | Repair dual duct CV mixing box pneumatics and calibrate AHU sensors |  |  | 94,704 | 39,000 | 15 | 15 | 1,420,560 | 585,000 | 63.30 | 20 |
| 3 | Clean AHU coils and fans and add pleated sealed filters |  |  | 69,195 | 88,928 | 5 | 5 | 345,975 | 444,639 | 46.20 | - |
| 4 | Repairs duct work air leaks |  |  | 19,087 | 15,562 | 10 | 10 | 190,870 | 155,624 | 12.70 | 2 |
| 5*A | Add/repair VFDs |  |  | 101,090 | 118,346 | 15 | 15 | 1,516,350 | 1,775,185 | 1.70 | 0.00 |
| 5*B | Set-Back/Set-forward control |  |  | 361,314 | - | 15 | 15 | 5,419,710 | - | 1.70 |  |
| Project level |  |  |  | 833,220 | 349,196 |  |  | 11,710,915 | 4,270,847 |  | 91 |
| 5* | : 2nd phase. Not included in the data base |  |  |  |  |  |  |  |  |
| Nexant Calculations: |  |  |  |  |  |  |  |  |
| EEM 1#: | Assumed the maximum tons | 1680 | tons |  |  |  |  |  |
|  | Average chiller efficiency | 0.65 | kW/ton |  |  |  |  |  |
|  | Estimated EFLH |  | 1000 | hrs | (Weather data) |  |  |  |
|  | Assumed maximum savings | 8% | (better estimation based on bill) |  |  |  |
|  | kWh savings = 1680 x 0.65 x 1000 x 8% = 87,360 kWh |
| EEM 2#: | Estimated dual duct AHUs airflow | 180,000 | cfm |  |  |  |  |  |
|  | corresponding estimated tonnage | 600 | tons |  |  |  |  |  |
|  | Average chiller efficiency | 0.65 | kW/ton |  |  |  |  |  |
|  | Estimated EFLH | 1000 | hrs |  |  |  |  |  |
|  | repairing mixing box can reduce chilled water consumption | 10% |  |  |  |  |
|  | kWh savings = 600 x 1000 x 0.65 x 10% = 39,000 kWh |
| EEM 3#: | assumed the supply fan head can be reduced by | 2% | after the coils were cleaned |  |  |
|  | total estimated fan power | 677 | kW |  |  |
|  | supply fan power account for | 75% |  |  |  |
|  | kWh savings = 677 x 75% x 2% x 8760 = 88,928 kWh |  |
| EEM 4#: |  |  |  |  |  |  |  |  |  |
|  | assumed air leakage |  | 0.01 |  |  |  |  |  |  |
|  | total estimated fan power |  | 677 | kW |  |  |  |  |  |
|  | supply fan power account for | 75% |  |  |  |  |  |  |
|  | repaired units account for | 70% |  |  |  |  |  |  |
|  | kWh savings = 677 x 75% x 70% x 0.01 x 8,760 = 88,928 kWh |
| EEM 5A#: | AC-1 to AC-5 occupied period operating hours | 2600 | hrs |  |  |  |  |
|  | AC-1 to AC-5 unoccupied period operating hours | 6160 | hrs |  |  |  |  |
|  | Total fans power of AC-1 to AC-5 |  | 56.7333 | kW |  |  |  |  |
|  | Baseline: inlet guide vane |  |  |  |  |  |  |  |  |
|  | Assume average fan speed during occupied | 70% |  |  |  |  |  |
|  | Assume average fan speed during unoccupied | 50% |  |  |  |  |  |
|  | kWh savings = 2600 x 56.7 x (1-70% x70%) +6160 x 56.7 x (1-50% x50%) = 118,346 kWh |  |

Nexant Calculations Summary:  project kWh savings reduced from 833,220 kWh to 349,196 kWh because

- Nexant found measure 5B was not implemented and excludes its savings

- Nexant estimates lower EFLH

- Nexant has different percentage savings estimation than in the project document based on site inspection and data collection.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-02-M-002 |
| Building Type | Manufacturing |
| Building Square Feet | 175,000 |
| Project Completion Date | 12/9/2002 |
| CL&P Annual Energy Savings (kWh) | 365,537.00 |
| CL&P Lifetime Energy Savings (kWh) | 4,479,125.00 |
| Total Incentives | $13,512.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 7/6/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Repair compressed air leaks | No-Waste Drains | Compressor Air Piping & Control Modification & a small dryer for 10hp com. |
| Measure Life (years) | 5 | 10 | 15 |
| Total Number of Units | 75 CFM | 5 | 1 |
| CL&P-reported kWh Savings | 83,491.00 | 33,804.00 | 183,801.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = 75CFM (2) Operating efficiency = 19kW/100cfm for single stage (3) Total planned leaking hours = hrs |  |  |
| Calculation Methodology for CL&P-reported Savings | air leaks CFMx0.19kw/cfmxhrs/year=75x0.19x =kWh/year | ( )cfmx0.19kW/cfmx8736kWh/year |  |
| Inspection Action Items | 1) Were all 75CFM leaks repaired? Show repair list. 2) What type of compressor? 3) Other leaks surveys performed? 4) Other leaks repairs performed? 5) Actual Compressor hours? 6) Collect all related compressor nameplates. 7) Collect all related compressor power and cfm operation data. 8) Collect each compressor control method. 9) What is actual CFM load? 10) Actual compressor operation hours | 1) What is the each old drain diameter? 2) What is the old drain timing second per or minutes? 3) Inspect and verify each drain has been replaced. 4) Compressor water cooled or air cooled? | 1) What is current compressor off shift hours (?) 2) What is actual 125hp and 10hp? Compressors real powers? 3) What are the service areas of the two compressors (125hp and 10hp); 4) How do the 2 compressors cooperate. |
| Inspection Findings | 1) Reported by the facility manager that this measure has been fully implemented. But he could not know where they were. 2) On site observation: Compressor discharge air pressure 90psig | 1) Reported by the facility manager that this measure has been fully implemented. 2) The facility manger did not know the locations of 5 drains. | 1) This measure has been fully implemented. 2) The computer area in another campus has very light compressed air demand at night. By repiping and control modification, the 10hp replaces big compressor operation at night when production is off. Night air use before program: 125 hp compressor; Night air use after program: 10hp compressor. |

| Measure # | 4 | 5 |
| --- | --- | --- |
| Measure Description | Dew Point Controls and pressure switch on Regenerative Dryer for purging and electric heating occurs only needed | Cooling Water Pump Starter and Interlock |
| Measure Life (years) | 15 | 15 |
| Total Number of Units |  | 1 |
| CL&P-reported kWh Savings | 56,432.00 | 8,009.00 |
| Assumptions in CL&P-reported Savings |  |  |
| Calculation Methodology for CL&P-reported Savings |  | 1.42kWx5640hrs/year(off) =8009kwh |
| Inspection Action Items | 1) Does the dew point controller work as desired? 2) Does pressure switch works as desired? 3) What is the dew point set point? 4) How often does the electric heating and purging happen? | 1) What is the current compressor and water pump off hours? 2) Collect cooling water pump nameplate. |
| Inspection Findings | 1) Reported by the facility manger that this measure has been fully implemented. 2) According to the facility manager, Before the program, the dryer has to operate 24/7 After the program, it only operate when needed. | 1) Reported by the facility manger that this measure has been fully implemented. 2) The facility manger did not know this cooling water pumps. According to the documents, this cooling pump is for 125hp compressor. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair compressed air leaks |  | 2,805 | 83,491 | 42,075 | 5 | 5 | 417,455 | 210,375 |  | 0.00 |
| 2 | No-Waste Drains |  | 2,805 | 33,804 | 31,446 | 10 | 10 | 338,040 | 314,455 |  | 0.00 |
| 3 | Compressor Air Piping & Control Modification |  | 2,805 | 183,801 | 172,761 | 15 | 15 | 2,757,015 | 2,591,418 |  | 0.00 |
| 4 | Dew Point Controls and pressure switch on Regenerative Dryer |  | 2,805 | 56,432 | 42,924 | 15 | 15 | 846,480 | 643,860 |  | 0.00 |
| 5 | Cooling Water Pump Starter and Interlock | off : 5640 | 2,805 | 8,009 | 8,456 | 15 | 15 | 120,135 | 126,842 |  | 0.00 |
| Project level |  |  |  | 365,537 | 297,662 |  |  | 4,479,125 | 3,886,949 | 0.00 | 0.00 |

| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Annual operation hours: | 2805 | hours/year |  |  |  |  |  |  |  |  |
| EEM 1#: | Assume compressor full load power | 103.61111 | kW |  |  |  |  |  |  |  |
|  | Compressor efficiency |  | 0.2 | kW/cfm | (the average of screw compressor operation efficiency) |  |  |
|  | Leakage repaired |  | 75 | cfm |  |  |  |  |  |  |  |
|  | kWh savings = 75 x 0.2 x 2805 = | 42,075 | kWh |  |  |  |  |  |  |  |  |
| EEM 2#: | Assume 5 old drain cycling | 10 | seconds on | 3 | minutes off |  |  |  |  |  |  |
|  | Drain pressure | 90 | psig |  |  |  |  |  |  |  |  |
|  | Drain diameter | 0.375 | inch |  |  |  |  |  |  |  |  |
|  | Airflow rate | 11.21 | cfm |  |  |  |  |  |  |  |  |
|  | kWh savings =11.21 x 0.2 x 2805= | 31,446 | kWh |  |  |  |  |  |  |  |  |
| EEM 3#: | 125hp compressor power at full load | 103.61 | kW |  |  |  |  |  |  |  |
|  | 125hp compressor power at no load | 20.72 | kW | (estimated at 20% power of full load) |  |  |  |
|  | Assume load/unload cycle at night demand | 20% | full load | (considering compressed air leakage) |  |  |  |
|  | Average 125 compressor night power need | 37.30 | kW |  |  |  |  |  |  |  |
|  | 10hp compressor power |  | 8.29 | kW |  |  |  |  |  |  |  |
|  | 125hp compressor cooling pump savings is calculated in EEM 5#. |  |  |  |  |  |  |  |
|  | Assume 125hp compressor dryer power has comparable power consumption with 10hp compressor dryer and cooling consumption |  |  |
|  | Night operating hours |  | 5955 |  |  |  |  |  |  |  |  |
|  | kWh savings =(37.30-8.29)x5955= | 172,761 | kWh |  |  |  |  |  |  |  |  |
| EEM 4#: | Dryer day time average power after program | 2.1 | kW |  |  |  |  |  |  |  |
|  | Dryer full load power |  | 7 | kW |  |  |  |  |  |  |  |
|  | Operation hours before program |  | 8760 | hrs |  |  |  |  |  |  |  |
|  | kWh savings= (7-2.1)x 8760 = | 42,924 | kWh |  |  |  |  |  |  |  |  |
| EEM 5#: | 125hp compressor off hours | 5955 | hours/year |  |  |  |  |  |  |  |  |
|  | cooling pump power | 1.42 | kW |  |  |  |  |  |  |  |  |

kWh savings= 5955 x 1.42 = 8,456 kWh

Related Equipments Information:

|  | Measure 1 |  |
| --- | --- | --- |
|  | Compressor 1 | Compressor 2 |
| Quantity | 1 | 1 |
| Manufacturer | Ingersoll Rand |  |
| Type | screw | reciprocating |
| Cooling type | Air cooled |  |
| Model/Seri./Size | XLE/JH2401/14 1/2 = 9x7 |  |
| HP | 125 | 10 |
| CFM rating |  |  |
| Pressure (psig) | 90 |  |
| Control type |  |  |
| Motor Manufacturer |  |  |
| Volt/Amp rating |  |  |
| Motor Model/Ser. |  |  |
| Motor Eff. |  |  |
| Energy rate (kW/cfm) |  |  |

| Measure 4 Regenerative Dryer Quantity 1 Type Manufacturer Pioneer Model PHE 350 Capacity (ton) Comp HP/Heater kW /7kW Condensing pressure 70 Energy Eff. (kW/ton) Operating Schedule | Measure 5 Air Comp. Cooling Pump Quantity 1 Type Manufacturer Model Volt/Amp rating 460/2.1 HP or kW 1.42 kW Motor Eff. Operating Schedule |
| --- | --- |

| Project Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-02-M-006 |
| Building Type | manufacturing |
| Building Square Feet |  |
| Project Completion Date | 5/2/2003 |
| CL&P Annual Energy Savings (kWh) | 273,145.00 |
| CL&P Lifetime Energy Savings (kWh) | 2,043,790.00 |
| Total Incentives | $14,668.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 9/7/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Repair compressed air leaks | No-Loss Drains |
| Measure Life (years) | 5 | 10 |
| Total Number of Units | 75 | 4 |
| CL&P-reported kWh Savings | 215036.00 | 19357.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = 128 CFM (2) Compressor on-hours: 1st shift = 2600 hrs; 2nd shift = 2704 hrs; off shift = 3456hrs (3) BASE: 1shift: 1# Comp: 68% load; 74% F/L kW 2# Comp: 50% load; 62% F/L kW 2shift: 1# Comp: 56% load; 66% F/L kW 2# Comp: 50% load; 62% F/L kW Off shift: 1# Comp: 65% load; 73% F/L kW 2# Comp: off. (4) EEM 1#: 1shift: 1# Comp: 66% load; 72% F/L kW 2# Comp: off 2shift: 1# Comp: 54% load; 64% F/L kW 2# Comp: off Off shift: 1# Comp: 15% load; 36% F/L kW 2# Comp: off. | 1) Coefficient of Flow= 0.50 (2) Diameter of orifice (dia.) = 5/16" in (3) Upstream pressure = 100.0 psig (4) average setting is 10 sec. on 2 minutes off (5) BASE: EEM 1# (6) EEM 2#: 1shift: 1# Comp: 56% load; 66% F/L kW 2# Comp: off 2shift: 1# Comp: 45% load; 60% F/L kW 2# Comp: off Off shift: 1# Comp: 6% load; 31% F/L kW 2# Comp: off. |
| Calculation Methodology for CL&P-reported Savings | air leak and thus power reduction on three shifts= (74%+62%-72%) x 44.3kW x 2600hrs + (66%+62%-64%)x 44.3kW x 2704hrs+(73%-36%)x 44.3kW x 3456hrs | Total of 25cfm air reduction of the four drains: each drain: 162cm x 50% x 10/130 sec. = 6.2 cfm kWh Savings = (72%-66%) x 44.3kW x 2600hrs + (64-60%)x 44.3kW x 2704hrs+(36%-31%)x 44.3kW x 3456hrs |
| Inspection Action Items | 1) Were all 75 (128CFM) leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) Actual Compressor on hours on three shifts? 5) What type of compressors? How are they controlled? 6) What are actual three shift hours? 7) Collect Quincy compressors operation data sheet? 8) Check if the two Quincys operate as planned. | 1) Old drain diameter 5/16"? 2) Old drain has timing 10 second per 2 minutes off? 3) Inspect the existence of each drain. |
| Inspection Findings | 1) According to the facility representative, - this measure has been fully implemented in 2003. - the facility production equipments have moved around inside the facility. It is hard to identify them. - the facility business has doubled since this project. - Typical leakage occurs at fittings. - about compressors operation: Currently at the peak load production, a 50hp Quincy compressor operates around 65% to 75% along with the 10 hp Q-D compressor. It is never found that two Quincy operating. Each Quincy compressor is modulated between 10hp and 50hp. | 1) The four new drains were all identified on site. 2) According to the facility representative, the old drains were estimated to drain every two minutes. |

| Measure # | 3 |
| --- | --- |
| Measure Description | Reduce Comp Run Time |
| Measure Life (years) | 20 |
| Total Number of Units | 1 |
| CL&P-reported kWh Savings | 38752.00 |
| Assumptions in CL&P-reported Savings | (1) Off-shift hours = 3456 (2) New G-D compressor = 9 kW; New Quincy QTS-3 compressor = 2.7 kW. (3) BASE: EEM 2# (4) EEM 3#: 1shift: 1# Comp: 56% load; 66% F/L kW 2# Comp: off 2shift: 1# Comp: 45% load; 60% F/L kW 2# Comp: off Off shift: 1# Comp: off 2# Comp: off G-D Comp: 27% load ; 40% F/L kW. New Quincy comp: 100% load ,100% kW |
| Calculation Methodology for CL&P-reported Savings | 1) 9kW G-D compressor with 27% load and 40% FL kW replace 44.3kW Quincy with 6% load and 31% F/LkW for 3456Hrs off-shift. 2) Plus a 2.7kW Quincy tank with 100% load and 180 hrs Savings =(31%x 44.3kW - 40% x 9kW - 2.7kWx 100%) x 3456 hrs |
| Inspection Action Items | 1) Did 10hp G-D compressor installed? What type? Get nameplate. 2) Did the flow controller installed to hold pressure at 100psig? 3) Is the power 9kW for G-D compressor? 4) Ask if the new Quincy and G-D operate as planned during off shift? |
| Inspection Findings | 1) This equipment has been installed and operates for the functions below: Sat 1:00pm to Sun 11:00pm - (1) thermostat requirement (6psig); (2) Holding machines even though there is no production. Sun 11:00pm to Sat 1:00pm - Operate in parallel with the two Quincy compressors for production and other usage. 2) According to the facility representative, before this equipment was installed, One 50hp Quincy had to run during Saturday and Sunday for small air demand. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair compressed air leaks | 8,736 | 8,760 | 215,036 | 217,610 | 5 | 5 | 1,075,180 | 1,088,050 | 24.50 | 24.84 |
| 2 | No-Loss Drains | 8,736 | 8,760 | 19,357 | 22,195 | 10 | 10 | 193,570 | 221,955 | 2.20 | 0.63 |
| 3 | Reduce Comp Run Time | 3,456 | 1,768 | 39,752 | 26,570 | 20 | 20 | 795,040 | 531,396 | 11.20 | 3.01 |
| Project level |  |  |  | 274,145 | 266,375 |  |  | 2,063,790 | 1,841,401 | 38 | 28.49 |

| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EEM 1#: | Total leakage hours | 8760 | hrs |  |  |  |  |  |  |  |  |
|  | Assumed total leakage rate | 128 | cfm |  |  |  |  |  |  |  |  |
|  | Compressor energy efficiency = | 0.1940729 | kW/cfm |  |  |  |  |  |  |  |  |
| EEM 2#: |  |  |  |  |  |  |  |  |  |  |  |
|  | (1) Coefficient of Flow= | 0.5 |  |  |  |  |  |  |  |  |  |
|  | (2) Diameter of orifice (dia.) = 0.25 in | 0.25 | in |  |  |  |  |  |  |  |  |
|  | (3) Total planned leaking hours = | 8760 | hrs |  |  |  |  |  |  |  |  |
|  | (4) Upstream pressure = | 115 | psig |  |  |  |  |  |  |  |  |
|  | (5) Average operating efficiency = | 0.19407291 | kW/cfm |  |  |  |  |  |  |  |
|  | (6) 4 old drain has timing 10 seconds every 180 seconds |  |  |  |  |  |  |  |  |
|  | (7) Each old leakage | 3.264 | cfm |  |  |  |  |  |  |  |  |
|  | (8) Total old leakage | 13.055556 | cfm |  |  |  |  |  |  |  |  |
| EEM 3#: | G-D new compressor operating hours during off-shift | 1768 | hrs |  |  |  |  |  |  |
|  | Assume the Quincy kept at the minimum power | 7.992 | kW |  |  |  |  |  |  |
|  | Assume the new compressor operate efficiency | 1.1 | % FL kW/% FL CFM |  |  |  |  |  |
|  | The Quincy operate efficiency during off-shift | 1.8 | % FL kW/% FL CFM |  |  |  |  |  |
|  | G-D new compressor operating hours during off-shift | 6992 | hrs |  |  |  |  |  |  |
|  | Assume the G-D operate at full load in day time operation | 8.28888889 | kW |  |  |  |  |  |  |
|  | Assume the new compressor operate efficiency | 1.1 | % FL kW/% FL CFM |  |  |  |  |  |
|  | The Quincy operate efficiency |  |  | 1.5 | % FL kW/% FL CFM |  |  |  |  |  |

Nexant Calculations Summary:  project kWh savings reduce from 274,145 kWh to 266,375 because of lower annual operating hours in measure 3# (3456 hrs to 1768hrs).

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-001 |
| Facility Type | Manufacturing (metal sheet production) |
| Building Square Feet | 500,000 |
| Project Completion Date | 10/25/2004 |
| CL&P Annual Energy Savings (kWh) | 263,412.00 |
| CL&P Lifetime Energy Savings (kWh) | 2,634,120.00 |
| Total Incentives | $57,328 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/6/2006 |
| Inspected By: | Yujie Cui |

Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database

| Measure # | 1 |
| --- | --- |
| Measure Description | Repair compressed air leaks |
| Measure Life (years) | 10 |
| Total Number of Units | 263 |
| CL&P-reported annual kWh Savings | 263,412.00 |
| Assumptions in CL&P-reported Savings | (1) Leakage repaired = 263 CFM (2) BHP becomes 47.25 hp when the pressure reduce to 80psig. (3) BASE LINE Load and hours are distributed below: Main Production: 2340 hours; 525 cfm 1#: 100% load and 100% power; 2#: 63.4% load and 70.5% power; 3#: 50% load and 62% power. Late Production: 3484 hours; 380 cfm 1#: 100% load and 100% power; 2#: 54.5% load and 65% power; 3#: off. High Peak: 1040 hours; 853 cfm 1#, 2#, 3#: 100% load and 100% power. Pressure is reduced to 80psig. (4) EEM1#: Reduce air flow by 263cfm. Main Production: 2340 hours; 262 cfm 1#: 56.5% load and 66% power; 2#: 50% load and 62% power; 3#: off. Late Production: 3484 hours; 117 cfm 1#: 47.6% full load and operate load/no load; 2#, 3#: off. High Peak: 1040 hours; 590 cfm 1#: 100% load and 100% power; 2#: 90% load and 90.9% power; 3#: 50% load and 62% power. |
| Calculation Methodology for CL&P-reported Savings | BASE LINE energy: (1) Main Production: 52.5 BHP x 0.746/0.93me (100% + 70.5%+ 62%) x 2340hrs (2) Late Production: 52.5 BHP x 0.746/0.93me (100% + 65%) x 3484hrs (3) High Peak: 47.25 BHP x 0.746/0.93me (100% + 100%+ 100%) x 1040hrs EEM1# energy: (1) Main Production: 52.5 BHP x 0.746/0.93me (66% + 62%) x 2340hrs (2) Late Production: 52.5 BHP x 0.746/0.93me ( 62%) x 3484hrs (3) High Peak: 52.5 BHP x 0.746/0.93me (100% + 90.9%+ 62%) x 1040hrs kWh savings = Base line - EEM 1# kW savings = 47.25BHP x 0.746/0.93me (100% + 100%+ 100%) - 52.5 BHP x 0.746/0.93me (100% + 90.9%+ 62%) |
| Inspection Action Items | 1) Were all 567 (263cfm) leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load in Main Production, Late Production and High Peak (Flow meter)? 5) Verify actual hours in peak, low demand and sanitary? 6) Verify if 3 compressors operate as in the calculation? 7) Collect compressor operation data sheet including power consumption at different CFM? 8) What is typical compressor operation pressure? 9) Check what type of compressor and its control method? |
| Inspection Findings | 1) On-site sampling check found one leakage. 2) According to the facility representative, - Part of the leakage was repaired by Yarde Metal, and part leakage was repaired by their contractor; - The facility keeps checking and repairing the leakage by themselves. - The three compressors are automatically sequencing by programs. - Never has more than 2 compressors operating at the same time currently. - Wood shop machines operating 5:00am to 1:30pm every day. 3) On site observations, - Two compressors out of the three compressors were on. One is 100% load, and one is in the unload mode. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 6,864 | 6,500 | 263,412 | 277,708 | 10 | 10 | 2,634,120 | 2,777,083 | 7.20 | 0.00 |
| Project level |  |  |  | 263,412 | 277,708 |  |  | 2,634,120 | 2,777,083 | 7.20 | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1# | full capacity hours per year | 2080 | hrs |  |  |  |  |  |  |  |  |
|  | Assumptions: |  |  |  |  |  |  |  |  |  |  |
|  | Total proposed leakage | 263 | cfm |  |  |  |  |  |  |  |  |
|  | Compressed air repair | 95% |  |  |  |  |  |  |  |  |  |
|  | Air cooled rotary screw compressor power |  | 0.171 | kW/cfm |  |  |  |  |  |  |
|  | Leakage is independent on machine operation |  |  |  |  |  |  |  |  |

kWh savings = 0.171 x 263 x 2080 x 95% = 277,708 kWh

Nexant Calculations summary: Project kWh savings increased from 263,412 kWh to 277,708 kWh because

- Nexant uses compressors power efficiency collected through site inspection which is different than the project document

- Nexant assumes load/no load control for compressors based on site inspection which is different than the project document

- Nexant uses different annual operating hours.

Related Equipment Information:

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  | Existing Equipment |  |  |
|  | Compressor 1 | Compressor 2 | Compressor 3 |
| Quantity | 1 | 1 | 1 |
| Manufacturer | Quincy | Quincy | Quincy |
| Type | Rotary Screw | Rotary Screw | Rotary Screw |
| Cooling type | Air | Air | Air |
| Model | (QSTI245ANA3IEE)QSI-245 P$ | (QSTI245ANA3IEE)QSI-245 P$ | (QSTI245ANA3IEE)QSI-245 P$ |
| Serial number | UNO47672 | UNO47672 | UNO47672 |
| HP/BHP/kW | 50/52.5/42.1 | 50/52.5/42.1 | 50/52.5/42.1 |
| CFM rating | 246 | 246 | 246 |
| Pressure (PSIG) | 110 | 110 | 110 |
| Control type | Sequenced VSD (load unload) | Sequenced VSD (load unload) | Sequenced VSD (load unload) |
| Motor Manufacturer |  |  |  |
| Motor model |  |  |  |
| Motorl Eff. | 93.0% | 93.0% | 93.0% |
| Energy rate (kW/cfm) | 0.171 | 0.171 | 0.171 |
| Dryer model |  |  |  |
| Dryer hp |  |  |  |
| Operating Schedule |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-04-M-018 |
| Building Type | Manufacturing (ceramic capacitors) |
| Building Square Feet | 84,000 |
| Completion Date | 11/23/2004 |
| CL&P Annual Energy Savings (kWh) | 250,441.00 |
| CL&P Lifetime Energy Savings (kWh) | 3,045,055.00 |
| Total Incentives | $30,181 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/23/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Repair compressed air leaks | No-Loss Drains | Replace air driven mixer with electricity driven mixer |
| Measure Life (years) | 5 | 10 | 15 |
| Total Number of Units | 91 | 5 | 7 |
| CL&P-reported kWh Savings | 123,178.00 | 19,134.00 | 108,129.00 |
| Assumptions in CL&P-reported Savings | (1) Leakage repaired = 75 CFM (2) )Operating efficiency: 0.17kW/cfm for full load; 0.20kW/cfm for 1/2 load. Average : 0.188kW/cfm (3) Total planned leaking hours = 8736 (4) Power at different loads: Full load: 81Bhp, 0.177kw/cfm 1/2 load: 46.2 Bhp, 0.20kW/cfm No load: 13.8Bhp, 0cfm (5) Load profile at 3 shifts: 1st: 375cfm, M-F 7am to 3pm, 2080 hrs, 100% load 2nd: 334cfm, M-F 3pm to 11pm, 2080 hrs, 89% load 3rd: 320cfm, M-F 11pm to 7am, 4576 hrs, 85% load (6) Fixed M.E. =0.912 | (1) Coefficient of Flow= 0.40 (2) Diameter of orifice (dia.) = 0.25 in (3) Total planned leaking hours = 8736 cfm (4) Upstream pressure = 100.0 psig (5) Average operating efficiency = 18.8kW/100cfm (6) Old drain has timing 10 seconds every 3 minutes? | (1) This motor 70% on cycle. (2) Total hours: 8736. (3) Air driven motors: 14.5 cfm @100psig in calculation. 0.188kW/cfm (4) Electric motor: 1/4 hp, eff. = 75% |
| Calculation Methodology for CL&P-reported Savings | Full load: 81Bhp/0.912 x 0.746 = 66.3kW, 375cfm 1/2 load: 46.2Bhp/0.912 x 0.746 = 37.8kW, 187.5cfm No load: 13.8Bhp/0.912 x 0.746 = 11.2kW Average: 0.188kW/cfm 75 cfm x 0.188kW/cfm x 8736 Hrs/year = 123,178 kWh/year | 1/4" orifice@100psig = 104cfm x 0.4 = 41.6 cfm 41.6cfm x 10 sec./180 sec. = 2.33 cfm (2.33 x 5)cfm x 0.188kW/cfm x 8736kWh/year = 19,134kWh | (1) Air motor: 0.188kW/cfm x 14.5 x 7 x 8736 x 70% = 116690kwh (2) Electricity motor: 0.20hp/.75 x 0.746 x 8736 x 70% = 8561 kWh Savings = (1) - (2) = 108,129 kWh |
| Inspection Action Items | 1) Were all 91 (75 cfm) leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What are the actual total hours with compressors on? 5) Verify 3 shift hours. 6) Verify actual CFM load profile in 3 shifts? 7) Collect compressor operation data (power versus airflow load %, and also efficiency versus airflow load %) 8) Collect compressor control method, discharge pressure | 1) Was old drain diameter 0.25"? 2) Check old drain has timing 10 seconds every 3 minutes? 3) Inspect each drain to verify its existence. 4) Check the Chicago compressor is water cooled or air cooled? 5) What should be actual coefficient of flow? 6) Check drains operation pressure. | (1) Verify air motor 14.5 cfm, or 80 psig or 100 psig in real motor operation. (2) Check if the mixer has been replaced. (3) Check if the motor control method is cycle? Check if 70% on cycle (4) Is the operation hours are 8736 (8760) ? |
| Inspection Findings | 1. Sample check found no leakage. 2. Report by the operator: - Before program, the compressor run full load all the time - Pressure of leakage location average 20-60 psig - All leakage was detected by ultrasonic leak detector - Annual hours: 6240 to 6656 3. On-site observation: The compressor staging cycle: 25 seconds half load / 20 seconds full load | 1. All the 5 drains have been installed 2. Drains timing based on the operator's guess: Pre-program : 6-10 seconds/15 minutes Pot-program: 4 - 5 times per day in Summer. 3. Pressure = 90 psig | 1. All 7 mixers have been replaced with electric motor. 2. Site observation: 1 mixer is unplugged; 2 were off. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 8,736 | 6,656 | 123,178 | 88,473 | 10 | 10 | 1,231,776 | 884,730 |  | 0.00 |
| 2 | No-Loss Drains | 8,736 | 6,656 | 19,134 | 13,837 | 10 | 10 | 191,336 | 138,375 |  | 0.00 |
| 3 | Replace air driven mixer with electricity driven mixer | 8,736 | 6,656 | 108129 | 83,634 | 15 | 15 | 1,621,935 | 1,254,510 |  | 0.00 |
| Project level |  |  | 250,440 | 185,944 |  |  | 3,045,047 | 2,277,614 |  | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | Motor Eff. | 0.912 |  |  |  |  |  |  |  |  |  |
|  | Pre program: | 6656 | Annl. Hrs | 55.95 | kW |  |  |  |  |  |  |
|  | Post program: | 6656 | Annl. Hrs | 43.83 | kW |  |  |  |  |  |  |
|  | kWh savings = (55.95 – 43.83) x 6656 / 0.912 = 88,473 kWh |  |  |
| EEM 2#: | (1) Coefficient of Flow= | 0.4 |  |  |  |  |  |  |  |  |  |
|  | (2) Diameter of orifice (dia.) = 0.25 in | 0.25 | in |  |  |  |  |  |  |  |  |
|  | (3) Total planned leaking hours = 6656 | hrs |  |  |  |  |  |  |  |  |
|  | (4) Upstream pressure = | 90 | psig |  |  |  |  |  |  |  |  |
|  | (5) Average operating efficiency = | 0.18 | kW/cfm |  |  |  |  |  |  |  |
|  | (6) Old drain has timing 10 seconds every 3 minutes; | Each leakage | 2.107 | cfm |  |  |  |  |  |
|  | kWh savings = 0.18 x 2.107 / 0.912 = 13,837 kWh |
| EEM 3# | (1) Motor on cycle | 70% |  |  |  |  |  |  |  |  |  |
|  | (2) Total annual hours: | 6,656 |  |  |  |  |  |  |  |  |  |
|  | (3) Air driven motors: | 14.5 | cfm |  |  |  |  |  |  |  |  |
|  | Water cooled reciprocating power | 0.18 | kW/cfm |  |  |  |  |  |  |  |  |
|  | (4) Electric motor: Eff | 75% |  |  |  |  |  |  |  |  |  |
|  |  | 0.25 | hp |  |  |  |  |  |  |  |  |
|  | kWh savings =(0.18 x 14.5 x 70% x 7 - 0.25 / 75% x 0.746 x 0.9) x 6656 = 83,634 kWh |

Nexant Calculations Summary:  project kWh savings reduced from 250,440 kWh to 185,944 kWh because of

- Lower annual operation hours based on site inspection

- Lower compressor load based on site inspection

- Lower system pressure based on site inspection

Related Equipment Information

|  | Measure 1 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Existing Equipment |  |  |  |  |
|  | Compressor 1 |  |  |  |  |
| Quantity | 1 |  |  |  |  |
| Manufacturer | Ingersoll Rand |  |  |  |  |
| Type | Reciprocating |  |  |  |  |
| Cooling type | Water cooled |  |  |  |  |
| Model/Ser. | 75 LLE/L0493 D88A |  |  |  |  |
| Size | 125 7.25x5 LL2A 75 |  |  |  |  |
| HP | 75 |  |  |  |  |
| CFM rating | 375 |  |  |  |  |
| Pressure (PSIG) | 125 |  |  |  |  |
| Control type | 3 stage unloading |  |  |  |  |
| Motor Manufacture | Duty Master |  |  |  |  |
| Motor model | S-440-Y/65B C03xPP30A26 |  |  |  |  |
| Mechanical Eff. | 91.20% |  |  |  |  |
| Energy rate (kW/cfm) | 0.17@full load; 0.20@1/2 load |  |  |  |  |
|  |  | Measure 2 |  |  |  |
|  | Drain 1 | Drain 2 | Drain 3 | Drain 4 | Drain 5 |
| Drain Equipment | LLE Intercooler | LLE After cooler | LLE wet receiver | T40 Wet receiver | Zeks Refrigerated Air Dryer |
| Quantity | 1 | 1 | 1 | 1 | 1 |
| Drain Diameter | 0.25 in | 0.25 in | 0.25 in | 0.25 in | 0.25 in |
| Pressure (psig) | 90 | 90 | 90 | 90 | 90 |
| open seconds every minutes |  |  |  |  |  |
| Installed (Y/N) | Y | Y | Y | Y | Y |
| New Drain Manufacturer | Drain All, Inc. | Drain All, Inc. | Drain All, Inc. | Drain All, Inc. | Drain All, Inc. |
| New Drain Model | 1700/50644 | 1700/50644 | 1700/50644 | 1700/50644 | 1700/50644 |
| Measure 3 |  |  |  |  |  |
|  | Existing Equipment | New Equipment |  |  |  |
|  | Pneumatic Motor | Electric Motor (DC) |  |  |  |
| Quantity | 7 | 7 |  |  |  |
| Type |  |  |  |  |  |
| Manufacturer | Gast | Lightning |  |  |  |
| Model |  | EV1P25 |  |  |  |
| Cat./Ser. |  | 123998PSP/33-24272135G1 |  |  |  |
| HP |  | 0.25 |  |  |  |
| RPM |  | 1800.00 |  |  |  |
| Power information |  | 2.5Amp; 9 volt |  |  |  |
| Frame/Insulation/Duty |  | 56C/F/K |  |  |  |
| CFM | 14.5 |  |  |  |  |
| Pressure (Psig) | 80 |  |  |  |  |
| Motor Eff. |  | 75% |  |  |  |
| Control method |  |  |  |  |  |
| Operating Schedule |  |  |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-03-M-002 |
| Building Type | Manufacturing |
| Building Square Feet | 26,000 |
| Project Completion Date | 12/8/2003 |
| CL&P Annual Energy Savings (kWh) | 201,376 |
| CL&P Lifetime Energy Savings (kWh) | 1,712,370 |
| Total Incentives | $54,448 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/1/2006 |
| Inspected By: | Peter McBride and Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Install 23 motorized dampers on process exhaust taps & interlock to machines. Install one VFD on existing 50HP Torrit exhaust /baghouse fan. Install one or more relief dampers near the end of the duct runs to supply enough air to maintain minimum required velocity. |
| Measure Life (years) | 15 |
| Total Number of Units | 23 dampers, 1 VFD |
| CL&P-reported kWh Savings | 201,376 |
| Assumptions in CL&P-reported Savings | 1) Operation hours: 1st shift: 2080 hrs 2nd shift: 2080 hrs 3rd shift: 2080 hrs Weekends: 2496 hrs 2) Airflow and power BASELINE: (1) 1st shift: 100% exhaust flow; 43.09hp/35.48 kW (2) 2nd shift: 100% exhaust flow; 43.09hp/35.48 kW (3) 3rd shift: 100% exhaust flow; 43.09hp/35.48 kW (4) Weekends: 100% exhaust flow; 43.09hp/35.48 kW EEM: (1) 1st shift: 80% exhaust flow; 25.14hp/20.06 kW (2) 2nd shift: 70% exhaust flow; 16.84hp/13.44 kW (3) 3rd shift: 60% exhaust flow; 10.66hp/8.51 kW (4) Weekends: 60% exhaust flow; 10.66hp/8.51 kW |
| Calculation Methodology for CL&P-reported Savings | 1) BASELINE Consumption: kW = 35.48 kWh = (3x 2080 + 2496) x 35.48 = 309,979 2) POST EEM Consumption: kW = 20.06 kWh = 2080 x (20.06 + 13.44 + 8.51) + 2496 x 8.51 = 108,603 kWh Savings = BASELINE - Post = 309,979 - 108,603 = 201,376 kW Savings = BASELINE - Post = 35.48 - 20.06 = 15.42 |
| Inspection Action Items | 1) Check the VFD has been installed on the 50-HP dust collector exhaust fan? 2) Check that 23 motorized dampers have been installed? 3) Check how many and where relief dampers have been installed? 4) Collect Draw exact exhaust system layout from the exhaust machines to the exhaust outside including dampers. 5) What is the common exhaust deck size downstream the 50 hp fan? 6) Collect the nameplate of the 50hp exhaust fan and associated motor. 7) Verify operation hours in the three shifts and weekends. 8) Collect the exhaust operation difference between three shifts and weekends. 9) Ask how the VFD is controlled? What is the control parameter value? 10) Ask how the relief dampers are controlled? What are the control values? 11) Ask the minimum exhaust air velocity requirement that the system is being controlled. 12) Check VFD speed and power on the VFD controller monitor if possible. Otherwise measure the power. 13) Trend VFD speed if possible. 14) ESCO name and contact number |
| Inspection Findings | 1) One polishing machine has been removed. 2) The VFD has been installed and is operating. 3) A relief air damper was installed at the end of main duct work to maintain the minimum airflow when all the machines are closed. 5) Exhaust air circulates following the path: Space air with machine exhaust -- Filter and collector -- Fan -- return to space. 4) Control set points based on the interview with the facility representative: Fan speed: fixed 40Hz. Relief damper position: fixed. 6) Operation data from the fan VFD controller: Speed 40Hz; rpm:1193; 5.7kW; Accumulated 183MWh, 21.27khrs; 7) Annual operation hours: 8760-12-4=8,744 hrs |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Upgrade compressor controls and install compressors sequencer | 8,736 | 8,744 | 201,376 | 178,672 | 15 | 15 | 3,020,640 | 2,680,085 | 15.40 | 20.4 |
| Project level |  |  |  | 201,376 | 178,672 |  |  | 3,020,640 | 2,680,085 | 15.40 | 20.4 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
|  | Annual operation hours | 8,744 | Hrs |  |  |  |  |  |  |  |  |
|  | Estimated average kW at 40 Hz | 8.60 | kW = | 183/21.27 |  |  |  |  |  |  |  |
|  | Estimated kW at 60Hz | 29.04 | kW = | 8.6/(40/60)3 |  |  |  |  |  |  |  |
|  | kWh savings = (29.04-8.6) x 8,744 =178,672 kWh |  |
|  | kW savings = 29.04 - 8.60 = 20.4 kW |  |  |  |  |

Nexant Calculations Summary: project kWh savings reduced from 201,376 kWh to 178,672 kWh because

- Nexant determines average kW with VFD installation based on actual accumulated kWh and operating hours in the VFD controller collected during site inspection while project report estimated it by load percentage.

- Nexant calculates baseline motor power on the basis of real frequency and real logged power which is lower than the project document.

Related Equipment Information

|  | Measure 1 |
| --- | --- |
|  | Existing Equipment |
|  | Torrit Exhaust Fan (Dust Collector Exhaust Fan) |
| Collector manufacturer | Torrit filter Downflow Oval1 |
| Quantity | 1 |
| Fan manufacturer | New York Blower |
| Fan Type | Backward inclined |
| Model | ACF/PLR FAN Class I-III |
| Shop No. | V03474 10C |
| Size | 27ACF |
| CFM capacity | 16000 |
| Fan Head (inch) | 14 @ 16000cfm |
| Motor HP/BHP | 50/43.09@16000cfm |
| rpm | 1770 |
| Control type | VFD |
| Motor Manufacture | BALD |
| Motor Model | Cat. M4115T |
| Motor Mechanical Eff. | 0.93 |
| Motor power factor | 0.85 |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-006 |
| Building Type | Industrial laundry |
| Building Square Feet | 40,500 |
| Project Completion Date | 9/20/2004 |
| CL&P Annual Energy Savings (kWh) | 198,608 |
| CL&P Lifetime Energy Savings (kWh) | 2,979,120 |
| Total Incentives | $9,825 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/14/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Blower to replace compressed air |
| Measure Life (years) | 15 |
| Total Number of Units |  |
| CL&P-reported kWh Savings | 198,608.00 |
| Assumptions in CL&P-reported Savings | (1) Production: 2 shifts; 5.5days/week; 4576hrs for production; 4184 for non-production. Tank sparging: 24/7 (2) 20 kW at full load for each compressor. (3) Air flow is reduced by 101cfm when supplied by blower. (4) Operating efficiency: BASE: Production: 87% full power at 80% CFM load. Non-production: 71% full power at 60% CFM load. EEM: Production: 55% full power at 40% CFM load. 4576hrs Non-production: 0%. 4184 hrs Blower: 100%. 8760hrs |
| Calculation Methodology for CL&P-reported Savings | 1) Baseline: 87% x 40kW x 4576 hrs + 71% x 40kW x 4184 hrs 2) EEM: 55% x 40kW x 4576 hrs + 100% x 3.35kW x 8760 hrs Savings = (1) - (2) |
| Inspection Action Items | (1) Verify that the blower has been installed. (2) Verify actual production hours. (3) Collect blower nameplate and data sheet. (4) Verify actual blower power and compressor power. (5) Check real compressor discharge pressure. (6) How does the blower operate currently? Does the compressor stops during blower operation? (7) What special function does the blower perform? |
| Inspection Findings | (1) The blower has been installed to continuously draw outside air to a waste water tank. Function: to float the dust in the tank to remove it during production hours. The air was provided by the 2 compressors before the program. (2) According to the operator, Before the program: 2 compressors continuously operated during production hours. After the program: only one compressor is needed and cycles every 7- 9 minutes (3 - 4 minutes on; 4 -5 minutes off) (3) Annual facility operation hours are 2,210. (4) On site observations: the blower was on; one compressor was on, but cycled on/off; one compressor was off |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Blower to replace compressed air | 8,760 | 2,210 | 198,608 | 63,917 | 15 | 15 | 2,979,120 | 958,753 | N/A | 15.30 |
| Project level |  |  |  | 198,608 | 63,917 |  |  | 2,979,120 | 958,753 | 0.00 | 15.30 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | Annual production hours | 2210 | hrs | each compressor power: | 18.65 | kW |  |  |  |  |
|  |  |  |  | blower power | 3.35 | kW |  |  |  |  |
|  | Pre program: | compressors annual power consumption: | 89213 | kWh | continuous operation |  |  |
|  | Post program: | 1 compressor annual power consumption: | 16727 | kWh | 3 minutes on and 5 minutes off (8 minutes cycle) |
|  |  | Blower fan annual power consumption: | 8569 | kWh |  |  |  |  |
|  | kWh savings = 89,213 – (16727 + 8569) = 63,917 kWh |
|  | kW savings = 18.65 – 3.35 = 15.30 kW |

Nexant calculations summary:  Project kWh savings reduced from 198,608 kWh to 63,917 kWh because

- Nexant uses lower annual operating hours  than in the project document

- Nexant determines post installation compressor power consumption by site observation of compressor on/off cycle which is different than the project document.

Related Equipment Information

|  | Measure 1 |  |
| --- | --- | --- |
|  | Existing Equipment | New Equipment |
|  | Compressor 1 | Blower |
| Quantity | 2 | 1 |
| Manufacturer | Kellogg-American (Comp Air) | Vortron |
| Type | Reciprocating |  |
| Cooling type | air cooled |  |
| Model | 462C (from document); A462TVX (from the owner) |  |
| Hp/BHP/kW | 25hp/24.07 | 7.5/4.0/3.35kW |
| CFM rating | 100 at 100 psig (estimated by Scales Air Compressor) |  |
| Pressure (PSIG) | 120 | 5 psig |
| Control type | Load/no load | 200 cfm at 5 psig |
| Motor manufacturer |  | Us. Electric Air |
| Motor model |  | S671 |
| Motor Eff. | 92.40% | 86.4% to 88.5% |
| Energy rate (kW/cfm) |  |  |
| Operating Schedule |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-04-M-013 |
| Building Type | Manufacturing |
| Building Square Feet | 107,936 |
| Completion Date | 11/23/2004 |
| CL&P Annual Energy Savings (kWh) | 183,495.00 |
| CL&P Lifetime Energy Savings (kWh) | 2,752,425.00 |
| Total Incentives | $53,460 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/13/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Upgrade compressor controls and install compressors sequencer |
| Measure Life (years) | 15 |
| Total Number of Units | 3 |
| CL&P-reported kWh Savings | 183,495.00 |
| Assumptions in CL&P-reported Savings | (1) Peak load: 1200cfm; Off-peak: 1000cfm (2) Peak hours: 2080hrs; Off-peak hours: 4576hrs (3) Pre EEM cfm load/Power load percentage: On-Peak: Compressor 1#: 80%/83%; Compressor 2#: 75%/95%; Compressor 3#: 91%/98%. Off-Peak: Compressor 1#: 75%/81%; Compressor 2#: 50%/87%; Compressor 3#: 74%/94%. (4) Post EEM cfm load/Power load percentage: On-Peak: Compressor 1#: 100%/100%; Compressor 2#: 96%/100%; Compressor 3#: off. Off-Peak: Compressor 1#: 100%/100%; Compressor 2#: 52%/82%; Compressor 3#: off. |
| Calculation Methodology for CL&P-reported Savings | 1) PRE EEM Consumption: ON-peak: 1#: 129.6kW x 83% x 2080hrs + 3.4kW x 2080 hrs 2#: 91.2kW x 95% x 2080hrs 3#: 49 kW x 98% x 2080hrs + 3.0kW x 2080 hrs OFF-peak: 1#: 129.6kW x 81% x 4576hrs + 3.4kW x 4576 hrs 2#: 91.2kW x 87% x 4576hrs 3#: 49 kW x 94% x 4576hrs + 3.0kW x 4576 hrs kW on peak: = 129.6x 83% + 91.2x 95% + 49x98%+3+3.4=248.6 kW off peak: = 129.6x 81%+91.2x 87%+49x 94%+3+3.4=236.8 2) POST EEM Consumption: ON-peak: 1#: 129.6kW x 100% x 2080hrs + 3.4kW x 2080 hrs 2#: 91.2kW x 100% x 2080hrs 3#: 0 OFF-peak: 1#: 129.6kW x 100% x 4576hrs + 3.4kW x 4576 hrs 2#: 91.2kW x 82% x 4576hrs 3#: 0 kW on peak: = 129.6x 100% + 91.2x100%+3.4= 224.2 kW off peak: = 129.6x 100% + 91.2x82%+3.4= 207.8 kWh Savings = Pre - Post = 183,496 on peak kW savings = Pre - Post = 24.2 off-peak kW savings = Pre - Post = 29 |
| Inspection Action Items | 1) Verify that the sequencer and electronic control have been installed? 2) What is the actual on-peak and off-peak hours? 3) What is actual on-peak and off-peak CFM load demand? 4) Collect operation data sheet especially power consumption at different CFM. 5) Verify each compressor load in pre EEM. 6) Check if the three compressors are currently sequenced as the calculation assumed. 7) Check each compressor control method to realize the assumed airflow load distribution in the calculations? 8) Collect compressors nameplates 9) Collect compressors operation datasheet (% FL kW vs. % FL CFM) |
| Inspection Findings | 1) One of the original three compressors has been removed and replaced by two identical smaller compressors. There are four compressors currently, three of which in the boiler room and the rest one (150hp) in Main room. The discharge pipes in the two rooms are connected to serve the whole plant. 2) The master sequencer has been installed to control the operation sequence of all four compressors. There is a slave sequencer in the 150hp compressor room for monitoring. 3) There are airflow sensors in each of the two rooms. 4) The total annual hours: 1# shift (peak load): 2080; 2# shift (50%load): 2080; 3# shift and Saturday (30%):2600 5) Pre-program compressors: no sequence control; all compressors operate at the same time and was modulated based on each modulation method. 6) Site observations (10:00am to 11:30am): - The 150hp and 60hp compressors were operating; power was 128kW and 43 kW separately. - Airflow Before Valve Pressure After Valve Pressure Boiler Room 163 cfm 100psig 90psig Main Room 602 cfm 100psig 90psig |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Upgrade compressor controls and install compressors sequencer | 6,656 | 6,760 | 183,496 | 311,923 | 15 | 15 | 2,752,425 | 4,678,838 | 0.00 | 24.97 |
| Project level |  |  | 183,496 | 311,923 |  |  | 2,752,425 | 4,678,838 | 0.00 | 24.97 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
|  | Annual hours | cfm | Post-program power | Pre-program power |  |  |  |  |  |
| 1# shift (peak load): | 2080 | 782 | 171 |  | 196.0 |  |  |  |  |  |  |
| 2# shift (50%load): | 2080 | 391 | 84.5 |  | 129.1 |  |  |  |  |  |  |
| 3# shift and Saturday (30%): | 2600 | 235 | 46.0 |  | 110.3 |  |  |  |  |  |  |
| kWh savings = = 311,923 kWh |  |  |  |  |  |
| kW savings = 196.0 -171 = 24.97 kW |  |  |  |  |  |
|  |  | Pre-program compressor operation |  |  |  |  |  |  |  |
|  | Full air flow | full power (kW) | 1st shift airflow | 1st shift power | 2nd shift airflow | 2nd shift power | 3rd shift airflow | 3rd shift power |  |  |
| Compressor 1# | 760 | 130 | 45% | 80.6 | 22% | 54.6 | 13% | 48.1 |  |  |  |
| Compressor 3# | 270 | 48 | 45% | 39.4 | 22% | 23.0 | 13% | 16.8 |  |  |  |
| Compressor 4# x 2 | 356 | 61.3 | 45% | 76.0 | 22% | 51.5 | 13% | 45.4 |  |  |  |
| total | 1742 | 300.6 |  | 196.0 |  | 129.1 |  | 110.3 |  |  |  |
|  |  | Post-program compressor operation |  |  |  |  |  |  |  |
|  | Full air flow | full power (kW) | 1st shift airflow | 1st shift power | 2nd shift power | 2nd shift power | 3rd shift airflow | 3rd shift power |  |  |  |
| Compressor 1# | 760 | 130 |  | 128 | 51% | 84.5 | 0% | 0 |  |  |  |
| Compressor 3# | 270 | 48 |  | 43 | 0% | 0.0 | 0% | 0 |  |  |  |
| Compressor 4# x 2 | 356 | 61.3 |  |  | 0% | 0.0 | 66% | 46.0 |  |  |  |
| total | 1742 | 300.6 |  | 171 |  | 84.5 |  | 46.0 |  |  |  |
| Note: The % power vs. % load are referred to App. 2.A.3 in Best Practices for Compressed Air Systems |  |  |

Nexant Calculations Summary: project kWh savings reduced from 183,496 kWh to 311,923 kWh because of

- different total airflow demand

- different number of shifts

- different shift load

- different total number of compressors

Related Equipment Information

|  | Existing Equipment | New Equipment |
| --- | --- | --- |
|  | Compressor 1 | Compressor 2 not existed anymore | Compressor 3 | Compressor 4 |
| Quantity | 1 | 1 | 1 | 2 |
| Manufacturer | Gardner Denver | Gardner Denver | Gardner Denver | Gardner Denver |
| Type | Rotary Screw |  | Rotary Screw | Rotary Screw |
| Cooling type | air cooled | water cooled | air cooled | Air cooled |
| Model | SAV - 150 | ES100 | ESII-60 (EBMQKC)/Se. U01224 | Electro-Saver 75 (ES-75) (EAM99C) |
| BHP/kW | 150/130 | 110/91.2 | 60/48 | 75/61.3 |
| CFM rating | 760 | 460 | 270 | 356 |
| Pressure (PSIG) | 100 |  | 100 | 100 |
| Control type | Variable displacement | modulation | modulation (Inlet ) | Variable displacement |
| Dryer Model |  |  | RSD1000, 1000cfm@100psig and 100F |  |
| Fan motor kW | 3.4 | No | 3 |  |
| Compressor motor Man. |  |  |  |  |
| Motor Model |  |  |  |  |
| Mechanical Eff. | 95.00% |  |  | 95.40% |
| Energy rate (kW/cfm) |  |  |  |  |
| Operating Schedule |  |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-03-M-005/01 |
| Building Type | Manufacturing |
| Building Square Feet | 50,000 |
| Completion date | 11/16/2004 |
| CL&P Annual Energy Savings (kWh) | 171,237.00 |
| CL&P Lifetime Energy Savings (kWh) | 1,712,370.00 |
| Total Incentives | $54,448 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/22/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Repair compressed air leaks | Install nozzles, regulator and sol valve |
| Measure Life (years) | 10 | 10 |
| Total Number of Units |  | 44 |
| CL&P-reported kWh Savings | 129,229 | 42,008 |
| Assumptions in CL&P-reported Savings | 208cfm leakage |  |
| Calculation Methodology for CL&P-reported Savings | Air leakage was measured |  |
| Inspection Action Items | 1) How many and how much cfm leaks have been repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load profile in different shift? 5) Verify actual hours in different shift? 6) Verify if compressors operate as in the calculation? 7) Collect each related compressor operation data sheet including power consumption at different CFM. 8) Collect each compressor nameplate. 9) Collect each compressor control method. 10) If there is more than one compressor, what is the control sequencing? | 1) Check all the nozzles, regulators and interlocked solenoid valves that have been replaced or installed? 2) Ask how these measures impact compressor operation? |
| Inspection Findings | 1) No leakage found by sampling. 2) Per the facility representative, the facility annual production hours are 4,000hours. 3) Site observations: - The tank pressure was controlled at 109psig. - VFD speed was between 48Hz and 35Hz when it was on. Mostly loading and no loading. - The sampled compressor loading/unloading cycle: 75 seconds loading - 100psig to 108psig; maintained at 35Hz. 40 seconds unloading - 108psig to 100psig; 48Hz to 35Hz. | 1) Sol valves and associated parts were found installed. 2) Based on the facility representative, each set of valve was closed when the controlled machined was turned down. |

| WE-03-M-005 Savings Summary |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 8,760 | 8,760 | 129,229 | 136,832 | 10 | 10 | 1,292,290 | 1,368,325 | 27.95 | 0.00 |
| 2 | Install nozzles, regulator and sol valve | 8,760 | 8,760 | 42,008 | 46,378 | 10 | 10 | 420,080 | 463,783 | 5.80 | 0.00 |
| Project level |  |  |  | 171,237 | 183,211 |  |  | 1,712,370 | 1,832,108 |  | 0.00 |
| Nexant calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM1 #: | Assumed annual hours |  | 4000 | hrs |  |  |  |  |  |  |  |
|  | Assumed compressor efficiency |  | 0.16446208 | kw/cfm |  |  |  |  |  |  |  |
|  | Assumed leakage rate: |  | 208 | cfm | (counted on the measured leakage by A &M Compressed Air Product) |  |  |
| EEM2#: | assumed leaked air |  | 70.5 | cfm | (counted on the measured leakage by A &M Compressed Air Product) |  |  |

| WE-03-M-005 Related Equipment Information |
| --- |
|  | Measure 1 |
|  | Existing |
|  | Compressor 1 |
| Quantity | 1 |
| Manufacturer | Ingersoll - Rand |
| Type | Screw |
| Cooling type | Air cooled |
| Model/Ser. | SSR-EPE100-2S / FF2085U01018 |
| HP/BHP/kW | 100/ |
| CFM rating | 504 |
| Pressure (PSIG) | 125 |
| Control type | load/unload/VFD |
| Fan power (hp) | 5 |
| Mechanical Eff. |  |
| Energy rate (kW/cfm) | 0.164462081 |
| Operating Schedule |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-008 |
| Building Type | Printing |
| Building Square Feet | 240,000 |
| Completion Date | 12/20/2004 |
| CL&P Annual Energy Savings (kWh) | 159,249.00 |
| CL&P Lifetime Energy Savings (kWh) | 2,547,976.00 |
| Total Incentives | $17,000 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/29/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Furnish and Install insulation piping and valves; Piping material to be copper $& insulated; Provide necessary glycol; connect M600 press & 100ton chiller |
| Measure Life (years) | 16 |
| Total Number of Units |  |
| CL&P-reported kWh Savings | 159,249 |
| Assumptions in CL&P-reported Savings | 1) Operation hours = 24hr x 5days x 52weeks + 6hr (sat) x 52week = 6552 hrs 2) Using 10F difference Bin hours. 3) Chiller eff. difference: Baseline chiller Premium Chiller Hrs ton kW/ton ton kW/ton 95F 3 30 1.4 78.3 1.2 90F 123 30 1.3 80.9 1.1 80F 520 30 1.2 75.7 1.0 70F 1016 30 1.2 81.1 0.9 60F 1061 30 1.1 86.9 0.7 --------------------------------------------------------------------------------------- total 2,723 4) Free Cooling hrs and cooler fan powers: Hrs # of fan operation Fan power kW 50F 954 2 3.5 40F 1101 2 3.5 30F 1035 1 1.75 20F 487 10F 202 0F 58 ----------------------------------------------------------------------------------------- total 3,837 5) In the base line chiller, 37kW is assumed for 3837hours. 6) Chiller and free cooler are switched when the outside air temperature is below 55F. |
| Calculation Methodology for CL&P-reported Savings | 1) When Chiller is used: savings is calculated by sum of (kW/ton difference x 30 tons x Bin hours) ((1.4-1.2) x 3 + (1.3-1.1) x123+(1.2-1.0) x520 +(1.2-0.9) x1016 +(113-0.7) x 1061) x 30 ton = 26,283kWh 2) When free cooler is used base line chiller = 37 kW x 3837hrs = 141969 kWh free cooler energy = 2 x 3.5kW x 954hrs + 3.5kW x 1101hrs + 1.75 x 1035hrs = 9003kWh Savings = 141969 - 9003 = 132,966kWh |
| Inspection Action Items | 1) Verify that the piping, insulation, valves and other measures are all actually installed and operated as incentives expect. 2) Specific nameplate for existing chiller and premium chiller/cooler? 3) What is fan power for the premium cooler? How many? 4) Get baseline chiller efficiency when the outside air temperature is lower than 55F. 5) Get premium chiller efficiency data (EERs) at different temperature when it operates at 50ton (before piping). 50ton process load consumption should also be different before and after piping. 6) Verify number of fan operation of free cooler under different temperature. 7) Verify actual load requirement for M600 Press. The provided measurement data indicates that average load is lower than 30 tons. 8) Collect the number of unit for this measure |
| Inspection Findings | 1) The piping, insulation, valves and other measures are all actually installed and operated as incentives expect. Small chiller (M600) is only for backup. 2) According to Mark, - 100 ton chiller and free cooler is automatically switched at the outside air temperature 45F; - Before the program, the small chiller operates year around while 100 ton chiller cycled on/off very frequently due to low load. - Supply water temperature set point is 55F with free cooler. - Current 100 ton chiller pumps have VFDs. 3) Site observations: - 100 ton chiller supply water temperature 45F; - Return water temperature 51F. 4) The outside air temperature at the visit day: around 80F. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Furnish and Install insulation piping and valves; connect M600 press & 100ton chiller | 6,560 | 6,864 | 159,245 | 138,865 | 16 | 16 | 2,547,920 | 2,221,836 | 4.60 | 9.24 |
| Project level | Project level |  |  | 159,245 | 138,865 |  |  | 2,547,920 | 2,221,836 | 4.60 | 9.24 |

| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EEM 1# | Annual operation hours: | 24x5x52x(9/12)+24x7x52x(3/12)=6864Hrs |  |  |  |  |  |
|  | M600 condensing pump | 15hp = 10.6 kW | Chilled water pump 7.5hp= 5.6 kW |  |  |  |
|  | Each free cooler fan power | 2hp = 1.5 kW |  |  |  |  |  |  |  |
|  | Mechanical chilling |  |  |  |  |  |  |  |  |  |  |
|  | Bin Temp (F) | Hrs | Tons | Small kW/ton | Big Tons (Pre) | Big kW/ton (pre) | Big Tons (post) | Big kW/ton (post) | Chiller savings | Pump power reduction | Pump savings |
|  | 95 | 3.2 | 30 | 1.4 | 30 | 1.26 | 60 | 1.2 | 25 | 3 | 10 |
|  | 90 | 129.5 | 30 | 1.3 | 30 | 1.155 | 60 | 1.1 | 990 | 3 | 419 |
|  | 80 | 547.4 | 30 | 1.2 | 30 | 1.05 | 60 | 1 | 4105 | 3 | 1773 |
|  | 70 | 1069.5 | 30 | 1.2 | 30 | 0.945 | 60 | 0.9 | 11069 | 3 | 3464 |
|  | 60 | 1116.8 | 30 | 1.1 | 30 | 0.735 | 60 | 0.7 | 14575 | 3 | 3618 |
|  | 50 | 1004.2 | 30 | 1 | 30 | 0.63 | 60 | 0.6 | 12954 | 3 | 3253 |
|  | Total |  |  |  |  |  |  |  | 43719 |  | 12537 |
|  | Free Cooling |  |  |  |  |  |  |  |  |  |  |
|  | Bin Temp (F) | Hrs | Small kW/ton | Cooling savings kWh | Extra # condensing fans | Fan power Penalty | Pump savings |  |  |  |  |
|  | 40 | 1158.9 | 0.9 | 31292 | 2 | 3458 | 5631 |  |  |  |  |
|  | 30 | 1089.5 | 0.8 | 26147 | 1 | 1625 | 5294 |  |  |  |  |
|  | 20 | 512.6 | 0.7 | 10765 |  |  | 2491 |  |  |  |  |
|  | 10 | 212.6 | 0.6 | 3827 |  |  | 1033 |  |  |  |  |
|  | 0 | 61.1 | 0.5 | 916 |  |  | 297 |  |  |  |  |
|  | Total |  |  | 72947 |  | 5084 | 14745 |  |  |  |  |
|  | Project kWh savings = 43719 + 12537 +72947 + 14745 – 5084 = 138,865 kWh |  |

Nexant Calculations Summary: Project kWh savings reduced from 159,245 kWh to 138,865 kWh because of smaller free cooling Bin range and bigger mechanical cooling Bin range based on site interview with the facility representative.

Related Chiller Information

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  |  | Existing Equipment |
|  | M600 Press (small press?) | Chiller/free cooler package (a closed loop with HX) |  |
| Quantity | 1 | 1 | 1 |
| Manufacturer | York | York | York |
| Type |  | Glycol cooler (glycol 40%) | Screw |
| Cooling type | Air Cooled | Air Cooled | Air Cooled |
| Model | YCAZ44LD8-46PC | SVCB241 |  |
| Ser. No | RKCM112001 |  | RDKM000025 |
| BHP/kW |  |  |  |
| Tonnage | 30 | 100 | 100 |
| CFM rating |  | 141,745 |  |
| Compressor/Fan HP | / 2 x 3 hp | 2 x 7 | 2 x / 12.0 LRA 3 x 2 fans |
| Compressor/Fan motor voltage | 460 |  |  |
| Compressor/Fan motor amps | 2 x 57 RLA, 293 RLA/ |  | RLA: 75/each; FLA 3.6/each/ |
| Condensing pump Hp | 15 |  | 20 |
| Chilled water pump Hp | 7.5 |  | 20 |
| Control type |  |  |  |
| Mechanical Eff. |  |  |  |
| Operating Schedule |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-01-M-007 |
| Building Type | Newspaper Manufactory |
| Building Square Feet | >50,000 |
| Project Completion Date | 7/9/2002 |
| Annual Energy Savings (kWh) | 126,501.00 |
| Lifetime Energy Savings (kWh) | 1,443,780.00 |
| Total Incentives | $24,815.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 9/12/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Add storage tank and regulator | Leak repairs |
| Measure Life (years) | 15 | 5 |
| Total Number of Units | 1 | 15 |
| CL&P-reported kWh Savings | 51,919.00 | 16,165.00 |
| Assumptions in CL&P-reported Savings | (1) 50% unregulated load occurs only on peak. (2) Full load pressure = 115psig (3) Ingersoll-Rand Model EP 75 compressor: 336CFM rating (4) On-peak load = 300 CFM; Off-peak load = 135 CFM (5) Regulate pressure from 115 psig to 90 psig (6) Peak hrs: 14hrs/day x 6 days/wk. x 52 wks/yr = 4368 hrs/yr. Off peak hrs: 3hrs/day x 6 days/wk. x 52 wks/yr = 936 hrs/yr. (7) Regulate load 50% (8) BASE: On-peak: 97% power with 90% CFM load; Off-peak: 82% power with 40% CFM load | (1) leakage repaired = 20 cfm (2) BASE = EEM#1 |
| Calculation Methodology for CL&P-reported Savings | (1) BASE: Peak: 81.3 Bhp/91.4%x0.746 x 97% x4368 hrs = 280, 910 kWh Off-peak: 81.3 Bhp/91.4%x0.746 x 82% x936hrs = 50,886 kWh (2) EEM 1#: New load with 50% regulated: 150cfm + 150cfm x (90+14.7)/(115+14.7) = 271 CFM On-peak: Load: 271/336 x (81.3 Bhp/91.4%x0.746) x 4368hrs = 233,705 kWh no-load: (1- 271/336) x 15.2kW x 4368hrs = 12,814 kWh off-peak: Load: 135/336 x (81.3 Bhp/91.4%x0.746) x 936 hrs = 24,822 kWh no-load: (1- 135/336) x 15.2kW x 936hrs = 8,536 kWh total: = 233,705+12,814+24,822+8,536 = 279,877 kWh kWh Savings = BASE - EEM 1# = (280, 910+ 50,886) -(233,705+12,814+24,822+8,536) = 51,919 kWh | Difference of total kWh before and after implementation of measure 2# BASE(EEM #1): 279,877kWh EEM 2#: On-peak: Load: 251/336 x (81.3 Bhp/91.4%x0.746) x 4368hrs = 216,330 kWh no-load: (1- 251/336) x 15.2kW x 4368hrs = 16,798 kWh off-peak: Load: 115/336 x (81.3 Bhp/91.4%x0.746) x 936 hrs = 21,223 kWh no-load: (1- 115/336) x 15.2kW x 936hrs = 9,361 kWh total: = 216,330+16,798+21,223+9,361 = 263,712 kWh Savings = BASE - EEM #2 = 16,165 kWh |
| Inspection Action Items | 1) What is actual % load needs to be regulated? 2) What is current on-peak and off-peak CFM load? 3) What is on-peak and off-peak CFM load period (total hours)? 4) Is full load pressure 115 psig or 100 psig? 5) Draw system piping with compressor and tank and regulator. 6) Get main compressor nameplate and operation data sheet (relation of cfm and kW). | 1) Were all 15 leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? |
| Inspection Findings | 1) This measure has been installed in the upstream of the production air loop and downstream of the two dryers and filters. 2) On-site observations: - Only the leading 50hp compressor was running during the visit at around 1:00pm. - The running compressor operating data: 30HZ, unloading, 64.7% capacity; 19.9 kW; discharge pressure 120 psig; accumulated operating hours 51,094. - Another 50hp compressor operating hours 10,740. | 1) No leakage was found by on-site sampling. 2) According to Bernard, the typical leaks occurred at the machine cracks in Press section. All the leaks were repaired by themselves. |

| Measure # | 3 | 4 | 5 |
| --- | --- | --- | --- |
| Measure Description | Replace 1/8" crimped copper tubing with nozzles | Add solenoid Valve for each machine | Replace timed drains with no waste drains |
| Measure Life (years) |  | 10 | 10 |
| Total Number of Units | 4 | 9 (actually 32=8 x 4) | 3 (actually 2) |
| CL&P-reported kWh Savings |  | 51,114.00 | 7,303.00 |
| Assumptions in CL&P-reported Savings |  | (1) Each machine down 6hrs/day (2) 6 down hours happens in on-peak period (3) Total waste = 180 cfm or 20cfm/each machine (4) BASE = EEM 1# & 2# | 1) Coefficient of Flow= 0.30 (2) Diameter of orifice (dia.) = 5/16" in (3) average setting is 10 sec. on every 3 minutes. (4) BASE: EEM 1#, 2# and 4# |
| Calculation Methodology for CL&P-reported Savings | This measure did not work per documentation | Average saved cfm = 180cfm x (6hrs/14hrs) = 77cfm new on-peak load = 251 cfm - 77cfm = 174cfm BASE: (measure 1# & 2#): =263,712 kWh EEM 4#: On-peak: Load: 174/336 x (81.3 Bhp/91.4%x0.746) x 4368hrs = 150,012 kWh no-load: (1- 174/336) x 15.2kW x 4368hrs = 32,002 kWh off-peak: Load: 115/336 x (81.3 Bhp/91.4%x0.746) x 936 hrs =21,223 kWh no-load: (1- 115/336) x 15.2kW x 936hrs = 9,361 kWh total: = 212,598 kWh Savings = BASE - EEM 4# | Total cfm air reduction of 3 drains: 162cm x 30% x 10/180 sec. x 3 = 2.7 cfm x 3 = 8.1 cfm New on peak load = 174 -8.1 = 166 cfm New off-peak load = 115 -8.1 = 107 cfm BASE =212,598 kWh EEM 5#: On-peak: Load: 166/336 x (81.3 Bhp/91.4%x0.746) x 4368hrs = 141,903 kWh no-load: (1- 166/336) x 15.2kW x 4368hrs = 33,860 kWh off-peak: Load: 107/336 x (81.3 Bhp/91.4%x0.746) x 936 hrs =19,858 kWh no-load: (1- 107/336) x 15.2kW x 936hrs = 9,674 kWh total: = 205,295 kWh Savings = BASE - EEM 5# |
| Inspection Action Items |  | 1) What is average down hours per day for each machine? 2) What is actual simultaneous down factors for 9 machines? 3) What is actual average reduced airflow rate? | 1) Old drain diameter 5/16"? 2) Old drain has timing 10 second every 3 minutes? 3) Inspect the existence of each drain. |
| Inspection Findings | 1) This measure has been implemented in 4 mail room stackers, one for each. 2) According to Bernard, - The nozzles are used to clean each stacker at the end of each shift of mailroom. There are 2 shifts per day. - The usage was 10 minutes/shift. - Air pressure is around 115psig. - Before this project, there was leakage at each tubing when it was not in use. | 1) This measure has been implemented in the press section. 2) According to Bernard, - Each valve was installed for each press machine. There are totally 4 presses with 8 press machines for each press. Actual total valve installed was 32 instead of 9. - Before the valves installation, there was leakage when each machine was shut off. | 1) This measure has been implemented. 2) Totally 2 new drains were found on site. |
| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Add storage tank and regulator | 5,304 | 8,760 | 51,919 | 43,572 | 15 | 15 | 778,785 | 653,584 |  | 0.00 |
| 2 | Repair Compressed Air Leaks | 5,304 | 8,760 | 16,165 | 33,072 | 5 | 5 | 80,825 | 165,358 |  | 0.00 |
| 3 | Replace 1/8" crimped copper tubing with nozzles |  | 8,760 |  | 3,307 |  | 5 |  | 16,536 |  | 0.00 |
| 4 | Add solenoid Valves | 5,304 | 8,760 | 51,114 | 52,915 | 10 | 10 | 511,140 | 529,147 |  | 0.00 |
| 5 | No-loss drain | 5,304 | 8,760 | 7,303 | 10,794 | 10 | 10 | 73,030 | 107,942 |  | 0.00 |
| Project level |  |  |  | 126,501 | 143,660 |  |  | 1,443,780 | 1,472,567 |  | - |

| Nexant Calculations: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| EEM 1# | assumed compressor efficiency increase | 20% |  |  |  |
|  | No load power | 19.9 | kW |  |  |  |
|  | Assume loading power | 29.84 | kW |  |  |  |
|  | averaging power | 24.87 | kW |  |  |  |
| EEM 2# | leak hours | 8760 | hrs |  |  |  |
|  | Assumed air leaks | 20 | cfm |  |  |  |
| EEM 3# | total repairing | 4 |  |  |  |  |
|  | assume leakage per tubing | 0.5 | cfm |  |  |  |
| EEM 4# | total vales | 32 |  |  |  |  |
|  | assume leakage per machine | 1 | cfm |  |  |  |
| EEM 5#: |  |  |  |  |  |  |
|  | (1) Coefficient of Flow= | 0.5 |  |  |  |  |
|  | (2) Diameter of orifice (dia.) = 0.25 in | 0.25 | in |  |  |  |
|  | (3) Total planned leaking hours = | 8760 | hrs |  |  |  |
|  | (4) Upstream pressure = | 115 | psig |  |  |  |
|  | (5) Average operating efficiency = | 0.1888 | kW/cfm | estimated to be 2 minutes cycle |
|  | (6) 2 old drain has timing 10 seconds every 180 seconds |  |  |  |
|  | (7) Each old leakage | 3.264 | cfm |  |  |  |
|  | (8) Total old leakage | 6.528 | cfm |  |  |  |

Nexant Calculation Summary: project kWh savings increased from 126,501kWh to 143,660kWh because

- Nexant uses higher total operating hours

- Nexant identified that EEM 3# has been installed which was not calculated in the project document.

Related Equipment Information:

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  | Existing Equipment |  |  |
|  | Compressor 1 (leading) | Compressor 2 (lag) | Compressor 3 (Backup) |
| Retrofitted Equipment | No | No | No |
| Quantity | 1 | 1 |  |
| Manufacturer | Ingersoll-Rand | Ingersoll-Rand | Ingersoll-Rand |
| Type | Rotary Screw | Rotary Screw | Rotary Screw |
| Cooling type | Water cooled | Water cooled | Water cooled |
| Model/Ser. | SSR-EPE50/CA1635U00242 | SSR-EPE50/CA1636U00242 | U38.4-SP/K849U91F |
| HP/BHP | 50/ | 50/ | 30/ |
| CFM rating | 208 | 208 | 125 |
| Volt/Amp rating | 460 | 460 |  |
| Pressure rating (psig) | 128psig/actual set point 115 psig | 128psig/actual set point 115 psig |  |
| Control type | VFD, leading in sequencing control | No VFD, lag in sequencing control |  |
| Energy rate (kW/cfm) | 0.188765182 | 0.188765182 |  |
| Operating Schedule | 24x7x365 | 24x7x365 |  |
|  | Measure 3 |  |  |
|  | Existing Equipment |  |  |
|  | Drain 1 | Drain 2 |  |
| Drain Equipment | Compressor 1 | Main Storage Tank |  |
| Quantity | 1 | 1 |  |
| New Drain Model/Ser. | Drain ALL-DR 3-C/MA-14243 | Drain ALL-DR 3-C/MA-14244 |  |
| Drain Diameter | 1/4" | 1/4" |  |
| Pressure (psig) | 115 | 115 |  |

| Production Section | Production Machines Capacity | Estimated airflow capacity | Annual Production hours |  | Machine use |
| --- | --- | --- | --- | --- | --- |
| Press | 4 sets of presses | 55% | Main Newspaper | 11:00pm to 4:00am (M-Sun) | 4 |
|  |  |  | Advance printing (ad.) | 5:00am to 11:00am (M-F) | 1.5 |
| Pre-press | 3 lines | 25% | Day time: | 7:00am to 5:00pm (M-Sun) | 1 |
|  |  |  | Night time: | 9:00pm to 1:00am (M-Sun) | 2 |
|  |  |  | Day time: | 5:00am to 11:00am (M-Sun) | 1.5 |
| Mailroom | 4 stackers | 20% | Night time: | 11:00pm to 4:00am (M-Sun) | 4 |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-02-M-003 |
| Facility Type | grocery store |
| Building Square Feet | 95,000 |
| Project Completion Date | 12/6/2002 |
| CL&P Annual Energy Savings (kWh) | 118,145.00 |
| CL&P Lifetime Energy Savings (kWh) | 2,717,335.00 |
| Total Incentives | $40,147 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 9/6/2006 |
| Inspected By: | Yujie Cui @ 914-609-0388 |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | 28F Meat Room evaporator air units | 3-inch foam core panel insulated door system | High speed door system for 28F interior cooler room |
| Measure Life (years) |  | 23 |  |
| Total Number of Units | 4 |  |  |
| CL&P-reported annual kWh Savings | 121,006.00 | 20,790.00 | 10,500.00 |
| Assumptions in CL&P-reported Savings | 1) Replace existing Kramer evaporator air unit with 4 New Vilter VLP-20-83 Industrial Air units. | 1) Furnish and install for the passage between the freezer and the 40F refrigerated space a 3-inch foam core panel door system without a defrost heater. |  |
| Calculation Methodology for CL&P-reported Savings | This measure is not implemented in the report document |  | This measure is not implemented in the report document |
| Inspection Action Items | 1) Check if the measure has been implemented? 2) Collect specifics for the old and new equipments. 3) What is the operation difference between the old and efficient equipment. | 1) Check if the measure has been implemented? 2) What is the impact of this measure? 3) Collect specifics for the old and new equipments. | 1) Check if the measure has been implemented? 2) Collect specifics for the old and new equipments. 3) What is the operation difference between the old and efficient equipment. |
| Inspection Findings | 1) This old units have been replaced with new units with hot gas by-pass defrost. 2) The old unit use electricity to defrost; the new unit use hot gas by-pass defrost. 3) According to the facility representative: - the reason to replace the old unit is because of its very low efficiency and weakness to withstand hot gas defrost. - the old unit defrosted 4 times/day and 30 minutes/defrost - the new unit defrosted 4 times/day and 22 minutes/defrost 4) On-site observations: The compressors that serve this function had the suction pressure 36.6 psig. | 1) This measure has been implemented. 2) This door is the entrance door for a -15F cooler. 3) The 3-inch insulated door system covers the outer layer of the cooler door. 4) On site measurement: the door size is 7' x 9'. 5) According to the facility representative: - There was ice on the outer surface of the door and the ground 6) On-site observations: - There was no ice on the ground and outer surface of the door - The compressors that serve this function had the suction pressure 8.0 psig. | 1) This measure should belong to project WE-02-M-016 2) On-site observations: The compressors that serve this function had the suction pressure 36.6 psig. |

| Measure # | 4 | 5 |
| --- | --- | --- |
| Measure Description | General impact door repair gasket | Hot gas by-pass for coils |
| Measure Life (years) | 23 | 23 |
| Total Number of Units | 44 | 10 |
| CL&P-reported annual kWh Savings | 60,428.00 | 36,927.00 |
| Assumptions in CL&P-reported Savings | 1) Perform repairs and replacement of seals, jambs, boots, panels and the like for the following rooms: Bakery, Milk Cooler, Egg cooler, 28F cooler, Deli Cooler, Produce Compactor/Receiving, Meat & Deli Prep | 1) |
| Calculation Methodology for CL&P-reported Savings |  |  |
| Inspection Action Items | 1) Check that all the doors have been fixed or replaced? (There is a list in the document?) 2) Collect specifics for the old and new equipments. 3) What is the operation difference between the old and efficient equipment. | 1) Check if this measure has been implemented in 10 Units? 2) Collect nameplates of the units which have been installed with hot gas by-pass on coils, especially power and capacity. 3) Inspect and collect data about the operation difference caused by this measure. |
| Inspection Findings | 1) The sample check found this measure has been implemented. | 1) This measure has been implemented even though 9 were identified on site: - 4 for the 28F meat room (see measure EEM1); - 4 for the deli cooler; - 1 for the fish cooler. |

| WE-02-M-01 Savings Summary |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | 28F Meat Room evaporator air units |  | 8,760 | 121,006 | 10,512 | 23 | 23 | 2,783,138 | 241,776 |  | 1.20 |
| 2 | 3-inch foam core panel insulated door system |  | 8,760 | 20,790 | 12,583 | 23 | 23 | 478,170 | 289,406 | 3.14 | 1.44 |
| 3 | High speed door system for 28F interior cooler room (this measure was not in the report document and database) |  | 8,760 | 10,500 |  |  |  |  |  |  |  |
| 4 | General impact door repair gasket |  | 8,760 | 60,428 | 67,437 | 23 | 23 | 1,389,844 | 1,551,041 | 9.12 | 7.70 |
| 5 | Hot gas by-pass by coils |  | 8,760 | 36,927 | 3,631 | 23 | 23 | 849,321 | 83,502 | 5.57 | 4.60 |
| Project level |  |  |  | 249,651 | 94,162 |  |  | 5,500,473 | 2,165,726 |  | 14.93 |

| Nexant calculations |  |  |  |  |
| --- | --- | --- | --- | --- |
| EEM1# | The unit capacity |  | 24000 | Btu/h |  |
|  | assumed new unit cooling efficiency (air cooled) | 1.2 | kW/ton |  |
|  | assume old unit efficiency |  | 1.8 | kW/ton |  |
| EEM2# | The insulated system heat transfer coefficient |  |  |  |
|  | Assume inner door heat transfer coefficient | 6 |  |  |
|  | Assumed door surface temperature without insulator 32 | F |  |
|  | Assumed room temperature | 70 | F |  |  |
|  | Door area | 63 | sq. feet |  |  |
| EEM4# | Total Gasket | 44 |  |  |  |
|  | assume each gasket has leakage | 9 | feet | by length |  |
|  |  | 0.1 | feet | by width |  |
|  | average leakage velocity | 1 | ft/sec |  |  |
|  | air density | 0.075 | lb/ft3 |  |  |
|  | room air temperature | 70 | F |  |  |
|  | average cooler temperature | 40 | F |  |  |
| EEM5# | 4 28F meat room blower units |  |  |  |  |
|  | old unit electricity for defrost | 6 | kW |  |  |
|  | Hot gas by-pass electricity use | 1.4 | kW |  |  |
|  | defrost cycle | 4 | times/day |  |  |
|  | electric defrost | 30 | minutes |  |  |
|  | hot gas defrost | 22 | minutes |  |  |
|  | 4 deli cooler blower units |  |  |  |  |
|  | 1 fish cooler |  |  |  |  |

Nexant Calculations Summary:  Nexant uses site inspection results to calculate savings combined with assumption.

Calculation methodology used:

General heat transfer loss = heat transfer coefficient x area x (Inner space temperature – outer temperature)

General heat loss due to infiltration = air density x leakage flow rate x (Inner space temperature – outer temperature)

kWh savings = Chiller kW/ton x heat loss (tons) x annual operating hours

kW savings = Chiller kW/ton x heat loss (tons)

| WE-02-M-003 Related Equipment Information |  |  |  |
| --- | --- | --- | --- |
| Measure 1#: |  |  |  |  |
|  |  | Ele. kW |  |  |
| Old evaporator unit: | KR66E-240--BAA | 6 |  |  |
| New evaporator unit (with hot gas by-pass): | KR66R-240--BA | 1.4 |  |  |
| Measure 5#: |  |  |  |  |
| The new refrigeration system that serves the measure EEM 1#- 5#: |  |  |
| total tonnage (ton): |  | 265 |  |  |
| compressors with 15F suction temperature (F): | 60 | 75 | hps |
| compressors with -22F suction temperature (F): | 20 | 25 | hps |
| compressors with -35F suction temperature (F): | 7.5 |  | hps |
| Refrigerant: | R-22 |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-01-M-004 |
| Facility Type | Warehouse |
| Building Square Feet | 512,000 |
| Project Completion Date | 12/21/2001 |
| CL&P Annual Energy Savings (kWh) | 114,583 |
| CL&P Lifetime Energy Savings (kWh) | 1,443,780 |
| Total Incentives | $22,352 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 5/25/2006 |
| Inspected By: | Dakers Gowans and Yujie Cui |

Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Variable Frequency Drive Control of Air Compressor | Variable Frequency Drive Control of Air Compressor | Replace Timer Operated Drains |
| Measure Life (years) | N/A | N/A | 5 |
| Total Number of Units | 1 | 1 | 6 |
| CL&P-reported kWh Savings | 31,575.00 | 18,881.00 | 14963.00 |
| Assumptions in CL&P-reported Savings | 40 hp | 20 hp |  |
| Calculation Methodology for CL&P-reported Savings | N/A | N/A | N/A |
| Inspection Action Items | 1) What is actual CFM load profile in different shift? 2) Verify actual 40hp compressor hours in different shift. 3) Verify if VFD is operating. 4) How is the VFD controlled? 5) Collect the 40hp compressor nameplate. 6) Collect each related compressor operation data sheet including power consumption at different CFM. 7) If there is more than one compressor, what is their control sequencing? 8) Collect compressor CFM load profile. | 1) What is actual CFM load profile in different shift? 2) Verify actual 40hp compressor hours in different shift. 3) Verify if VFD is operating. 4) How is the VFD controlled? 5) Collect the 20hp compressor nameplate. 6) Collect each related compressor operation data sheet including power consumption at different CFM. 7) If there is more than one compressor, what is their control sequencing? 8) Collect compressor CFM load profile. | 1) What is each old drain diameter? 2) What is the old drain timing? 3) Inspect and verify each drain has been replaced. 4) Which compressors provide air for these drains? These compressors are water cooled for air cooled? Pressure? |
| Inspection Findings | 1) The compressor currently operates every other week. 2) Observations: pressure: 95-100psi off on the visit. 3) Annual operation hours: 5,448/2=2,724 | 1) Old 20Hp compressor has been replace by a new 40hp compressor 2) The compressor currently operates every other week. 3) Site observations: pressure: 95-100psi VFD=25Hz; 22% capacity; 170F air outlet (at 10:00am 5/25/2006) 4) Annual operation hours: 5,448/2=2,724 | 1) 8 Drains were replaced instead of 6 |

| Measure # | 4 | 5 | 6 |
| --- | --- | --- | --- |
| Measure Description | Air Storage with Pressure Regulator | Interlock Dryers with Air Compressors | Install Timer on Reciprocating Compressor |
| Measure Life (years) | 15 | 10 | 10 |
| Total Number of Units | 1 | 1 | 1 |
| CL&P-reported kWh Savings | 23116.00 | 16996 | 9052.00 |
| Assumptions in CL&P-reported Savings |  |  |  |
| Calculation Methodology for CL&P-reported Savings | N/A | N/A | N/A |
| Inspection Action Items | 1) Verify that 600gal of air storage tank has been installed and operating? 2) What is the current system pressure? What is before? 3) How the pressure is regulated? 4) Which compressors link with the regulator? Draw the loop if needed. | 1) Verify which dryers have been interlocked with which compressors. 2) Collect the nameplates for the dryers with newly installed interlock (especially power). 3) Ask the dryers or interlocked compressors operation hours. | 1) Verify which reciprocating compressor has been installed with the timer? 2) Collect the nameplates for this compressor (especially power). 3) Ask the operation hours of this compressor. 4) Collect nameplate of this compressor (including type, power ...). 5) Verify control method of this compressor. 6) Verify how the timer has impacted the compressor operation hours. |
| Inspection Findings | 1) The tank and associated parts have been installed. 2) Tank pressure was observed to be 90-95psi | 1) Both the old and new compressors have been implemented. | 1) The timer has been installed in the compressor. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kW) | Lifetime | Lifetime Electricity Savings | Demand Savings |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Variable Frequency Drive Control of Air Compressor |  | 2,724 | 31,575 | 27,532 | 15 | 15 | 473,625 | 412,976 | 0.00 | 0.00 |
| 2 | Variable Frequency Drive Control of Air Compressor |  | 2,724 | 18,881 | 27,532 | 15 | 15 | 283,215 | 412,976 | 0.00 | 0.00 |
| 3 | Replace Timer Operated Drains |  | 2,724 | 14,963 | 16,908 | 5 | 5 | 74,815 | 84,541 | 0.00 | 0.00 |
| 4 | Air Storage with Pressure Regulator |  | 5,448 | 23,116 | 31,465 | 15 | 15 | 346,740 | 471,973 | 0.00 | 5.78 |
| 5 | Interlock Dryers with Air Compressors |  | 2,724 | 16,996 | 8,105 | 10 | 10 | 169,960 | 81,051 | 0.00 | 0.00 |
| 6 | Install Timer on Reciprocating Compressor |  | 5,448 | 9,052 | 4,572 | 10 | 10 | 90,520 | 45,722 | 0.00 | 0.00 |
| Project level |  |  |  | 114,583 | 116,114 |  |  | 1,438,875 | 1,509,240 | 0.00 | 5.78 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM1#, 2#: | assume average capacity | 50% | 40hp |  |  |  |  |
|  |  | Motor efficiency: 93% |  |  |  |  |
|  | Assume base is with inept modulation; Rotary screw compressor with VFD |  |  |  |  |
| EEM3#: |  |  |  |  |  |  |  |  |  |
|  | Drain size | 3/8" x 7 | Base cfm @100psi = | 34.48421 | cfm |  |
|  | Assume 1) old drains have timing 10 seconds on and 3 minutes off |  |
|  | 2) flow coeff =0.4 |  |  |  |  |
|  | 3) kw/cfm= 0.18 |  |  |
|  | 4) 8th drain seldom used |
| EEM4#: | assume pressure reduced from 125psig to 100psig |  |  |  |  |  |  |  |  |
|  | Motor efficiency 93% |  |  |  |  |  |  |  |  |
| EEM5#: | Assume dryer 2hp/each |  |  |  |  |  |  |  |  |  |  |
|  | Annual operating hours in the base line 8760 hours. |  |  |  |  |  |  |  |
| EEM6#: | reciprocating compressor 10hp; power consumption is | 36577.872 | when operating 5448 hours |  |  |  |  |
|  | Assume idle power is 20% full load power at 50% of the production operation time. |  |  |  |  |  |  |

Related Equipment Information

| Measure 1 Existing Equipment Compressor 1 Quantity 1 Manufacturer Quincy Type Screw Cooling type Air Cooled Model QST40ANA22P HP 40 CFM rating Pressure (PSIG) 100 Control type VFD Motor Manufacturer Toshiba Motor Model B0404PLF1YN101 Motor Mechanical Eff. Energy rate (kW/cfm) Operating Schedule two weeks per month Contact information 203-630-5555 | Measure 2 New Equipment Compressor 1 Quantity 1 Manufacturer Quincy Type Screw Cooling type Air Cooled Model QST40ACA31SR (Ser.92971J ) HP 40 CFM rating Pressure (PSIG) 100 Control type VFD Motor Manufacturer Motor Model Mechanical Eff. 93.00% Dryer Power (hp) 2 + 1/8 Energy rate (kW/cfm) Operating Schedule two weeks per month Contact Information (516)2489-096; (718)343-5656 |
| --- | --- |

|  | Measure 3 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Existing Equipment |  |  |
|  | Timer Drain 1 | Timer Drain 2 | Timer Drain 3 | Timer Drain 4 | Timer Drain 5 |
| Equipment | Existing compressor | New compressor | New Dryer | Dryer HG-75 | Maintenance Dryer |
| Quantity | 1 | 2 | 2 | 2 | 1 |
| Diameter estimation | 3/8" | 3/8" | 3/8" | 3/8" | 3/8" |
| Replaced | Yes | Yes | Yes | Yes | Yes |
| old drain timing second per or minutes |  |  |  |  |  |
| compressor type | Screw | Screw |  |  |  |
| Compressed air pressure | 95-100psi | 95-100psi | 95-100psi | 95-100psi | 95-100psi |
| Manufacturer/Model | ACCU/ACD3 |  |  |  |  |

| Measure 4 New Equipment Compressor 1, 2 Quantity 1 600 gallons air storage | Measure 6 Existing Equipment Compressor Quantity 1 Manufacturer Comp Air Type Reciprocating Cooling type Model DB452B HP 10 CFM rating Pressure (PSIG) Control type Motor Manufacturer BALDOR Motor Model CAT: FN3313T; 37E28ot33 Mechanical Eff. 87.00% Energy rate (kW/cfm) Operating Schedule occasionally |
| --- | --- |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-02-M-014 |
| Facility Type | Manufacturing |
| Building Square Feet | 164,500 |
| Project Completion Date | 12/2/2002 |
| CL&P Annual Energy Savings (kWh) | 105,583.00 |
| CL&P Lifetime Energy Savings (kWh) | 1,055,830.00 |
| Total Incentives | $2,750.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/29/2006 |
| Inspected By: | Peter McBride |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Automatic Condensate Drains |
| Measure Life (years) | 10 |
| Total Number of Units | 5 |
| CL&P-reported kWh Savings | 105,583.00 |
| Assumptions in CL&P-reported Savings | (1) Coefficient of Flow= (2) Diameter of orifice (dia.) = in (3) Total planned leaking hours = (4) Upstream pressure = psig (5) Old drain has timing seconds on and minutes off? (6) EEM2#: Reduce air flow by cfm. PEAK operation: cfm |
| Calculation Methodology for CL&P-reported Savings | 5 Drains: " orifice@ psig = cfm x 0. x sec./ sec. = cfm/each Total = cfm air can be reduced BASE LINE energy = EEM1# energy: EEM2# energy: (1) PEAK: |
| Inspection Action Items | 1) What was old drain diameter? 2) Check if old timer drains had timing seconds on and minutes off? 3) Inspect each drain to verify its existence. 4) What should be actual coefficient of flow? 5) Check the actual system pressure. 6) Collect compressor nameplates serving these drains. 7) Check compressor operation data (%kW vs. %cfm) 8) Verify the compressors control methods, sequencing if applicable. 9) Compressor operation hours. |
| Inspection Findings | 1. Five drains were found installed as reported. Two (2) of them are for the backup compressor Joy which seldom operates. 2. There are two compressors: Joy and Ingersoll-Rand 3. Based the facility manager, the Ingersoll-rand compressor does not operate during the evening. 4. On site observations: - Only the Ingersoll-Rand compressor was running. - Actual compressor discharge air pressure was 111psig. - The dryer output pressure was 117psig. |

| WE-02-M-014 Savings Summary |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings kW) |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | No-Loss Drains | 8,760 | 3,182 | 105,583 | 34,080 | 10 | 10 | 1,055,830 | 340,799 |  | 0.00 |
| Project level |  |  |  | 105,583 | 34,080 |  |  | 1,055,830 | 340,799 |  | 0.00 |

| Nexant calculations |  |  |  |  |
| --- | --- | --- | --- | --- |
| EEM 1#: | (1) Coefficient of Flow= | 0.65 |  |  |  |
|  | (2) Diameter of orifice (dia.) = 0.25 in | 0.25 | in |  |  |
|  | (3) Total planned leaking hours = | 3182.4 | hrs |  |  |
|  | (4) Upstream pressure = | 110 | psig |  |  |
|  | (5) Average operating efficiency = | 0.174957447 | kW/cfm |  |  |
|  | (6) 4 old drain has timing 15 seconds every 90 seconds; one old drain has timing 15 seconds every 30 seconds |
|  | (7) Each old leakage | 12.242 | cfm | 36.725 | cfm |
|  | (8) Total old leakage | 61.20833333 | cfm |  |  |
|  | kWh savings = total old leakage (cfm) x average operating efficiency (kW/cfm) x annual hours (hrs) = 34,080 kWh |

| Related Equipment Information |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | Measure 1 |  |  |  |
|  |  | Existing Equipment |  |  |  |
|  | Drain 1 | Drain 2 | Drain 3 | Drain 4 | Drain 5 |
| Drain Equipment | Joy Aftercooler | Joy Intercooler | dryer | prefilter | Afterfilter |
| Quantity | 1 | 1 | 1 | 1 | 1 |
| Drain Diameter | 1/4" | 1/4" | 1/4" | 1/4" | 1/4" |
| Pressure (psig) | 0 | 0 | 117 | 117 | 117 |
| Old Drain cycling | 15 seconds every 90 seconds | 15 seconds every 90 seconds | 15 seconds every 30 seconds | 15 seconds every 90 seconds | 15 seconds every 90 seconds |
| New Drain Model | Drain all 1700 | Drain all 1700 | Drain all 1700 | Drain all 1700 | Drain all 1700 |

|  | Measure 1 |  |
| --- | --- | --- |
|  | Existing Equipment |
|  | Compressor 1 | Compressor 2 |
| Quantity | 1 | 1 |
| Manufacturer | Joy (only for backup) | Ingersoll Rand |
| Type |  | rotary screw |
| Cooling type |  | air |
| Model/Ser. |  | SSR-HPE100-2S/FF2261001301 |
| BHP/kW | 102hp/82.23kW@full load; 23.46hp/18.91kW@no load |
| CFM rating |  | 470 FADCM |
| Pressure (PSIG) |  | 140psig |
| Control type |  | Load/unload VFD? |
| Mechanical Eff. |  |  |
| Energy rate (kW/cfm) |  | 0.174957447 |
| Operating Schedule |  | 24/7 |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-02-M-010 |
| Facility Type | Manufacturing |
| Building Square Feet | >200,000 |
| Project Completion Date | 1/16/2003 |
| CL&P Annual Energy Savings (kWh) | 94,760.00 |
| CL&P Lifetime Energy Savings (kWh) | 473,800.00 |
| Total Incentives | $1,760 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/10/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Repair compressed air leaks |
| Measure Life (years) | 5 |
| Total Number of Units | 75 |
| CL&P-reported annual kWh Savings | 94,760.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = 51CFM (2) Baseline airflow = 197CFM; (3) Annual operation hours: 8568 hours (4) Full load: 82.5hp; no load: 16kW |
| Calculation Methodology for CL&P-reported Savings | BASE LINE energy: Compressor: 82.5 BHP/0.923 x 0.746 x 100% x 8568 hrs Fan motor: 5 BHP/0.85 x 0.746 x 100% x 8568 hrs EEM1# energy: Airflow = 197 - 51 =146 CFM = 74% full airflow load Compressor loading: 82.5 BHP/0.923 x 0.746 x 74% x 8568 hrs Compressor no-loading: 16 kW x (1-74%) x 8568 hrs Fan motor: 5 BHP/0.85 x 0.746 x 100% x 8568 hrs kWh savings = Base line - EEM 1# |
| Inspection Action Items | 1) Were all 75 leaks (51 CFM) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load? 5) Verify actual hours? 6) Collect complete compressor operation data sheet including power consumption at different CFM? No load power? 7) What is typical compressor operation pressure? |
| Inspection Findings | According to the facility manager, 1) There are 3 compressors in parallel operation providing compressed air through the entire production lines and research department. The compressed air lines spread by branches instead of a closed loop through the entire production areas. The end of branches is short of enough pressures sometimes. 2) The 3 compressors are enabled 24/7. Compressor 1# (75hp) is the main compressor; Compressor 2# (50hp Ingersoll Rand) is the backup; Compressor 3# (50hp Kaeser) runs if the Research Department which is at the end of the pipe line does not have enough air pressure. 3) There are 2 departments operate equivalent to 6 days a week, which accounts for about 40% of total air demand. 4) He did not know any situations before this program since he joined this facility two years ago. On-site observations: 1) There was no leakage found by on-site sampling. 2) The 75-hp main compressor 1# and 50-hp Kaeser compressor 3# were running. The compressor 2# (50-hp Ingersoll Rand) was off during the site visit. It was reported by the technician that the he seldom saw the compressor 2# running. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 8,568 | 7,512 | 94,760 | 79,389 | 5 | 5 | 473,800 | 396,947 |  | 0.00 |
| Project level |  |  |  | 94,760 | 79,389 |  |  | 473,800 | 396,947 |  | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM1# | Main compressor (1#) estimated kW/cfm | 0.2072222 | kW/cfm |  |  |  |  |  |  |  |
|  | Assume leakage repaired | 51 | cfm |  |  |  |  |  |  |  |
|  | annual compressor loading hours | 7512 | hrs |  |  |  |  |  |  |  |

Nexant Calculations Summary: project kWh savings reduced from 94,760 kWh to 79,389 kWh because of

- Lower annual operating hours (8568 to 7512)

- Different calculation methodology.

Related Equipment Information

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  | Existing Equipment |  |  |
|  | Compressor 1 (Main Compressor) | Compressor 2 (Backup) | Compressor 3 |
| Quantity | 1 | 1 | 1 |
| Manufacturer | Le ROI Dresser | Ingersoll Rand | Kaeser |
| Type | Rotary Screw | Rotary Screw | Rotary Screw |
| Cooling type | Air cooled | Air cooled | Air cooled |
| Model/Ser. | WE75 SS II | SSR-EP50SE/G3867U95233 | BS61/510272 |
| HP | 75 | 50 | 50 |
| CFM rating |  | 194 scfm | 240scfm |
| Pressure (PSIG) | 109psig monitored | 125 psig | 110 psig (102-112psig) |
| Fan motor HP (if air cooled) | 3 | 3 | 3 |
| Control type | Load/no load |  |  |
| Motor Eff. | 92.3% |  |  |
| Dryer Model | Le ROI / LR 300 |  |  |
| Dryer power (hp) | 1.5 | 1.0 | 1.5 |
| Dryer airflow rate | 300 scfm@100 psig & 100F (Refrigerant R-12) |  | R-12 |
| Energy rate (kW/cfm) | 0.207222222 | 0.213631157 | 0.172685185 |
| Operating Schedule |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-004 |
| Building Type | Manufacturing |
| Square Feet | 380,000 |
| Project Completion Date | 12/14/2004 |
| CL&P Annual Energy Savings (kWh) | 91,657.00 |
| CL&P Lifetime Energy Savings (kWh) | 1,131,075.00 |
| Total Incentives | $19,779 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 7/18/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Tag and repair compressed air leaks & Reduce Air Pressure by 10 psig at Compressor | Add 1,550 Gallons of Air Storage to Existing 1,000 Gallons |
| Measure Life (years) | 10 (or 5) | 15 |
| Total Number of Units | 147 | 1 |
| CL&P-reported kWh Savings | 48,756.00 | 42,901.00 |
| Assumptions in CL&P-reported Savings | (1) Leakage repaired = 112.9 CFM (2) Operation hours = 8760 (3) Energy eff. =0.18kW/cfm (4) Existing pressure = 115psig; Proposed pressure = 105psig. (5) Base line annual energy = 385,080kWh | 1) Energy savings is 7% 2) Base line annual energy = 385,080kWh |
| Calculation Methodology for CL&P-reported Savings | 1) Savings due to repair leakage: 112.9 cfm x 0.18 kW/cfm x 8760 hrs = 178,021 kWh Demand savings: 112.9 cfm x 0.18 kW/cfm = 20.32kW 2) Savings due to reduce pressure from 115psig to105psig: 385080kWh x 5% = 19,254kWh. Total = (1) + (2) = 197,275 kWh | Energy savings: 7% x 385,080kWh = 26,955 kWh |
| Inspection Action Items | 1) Were all leaks repaired? If not, where were repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) How many shifts? What is the schedule in each shift? 5) What are the actual compressor operation hours? 6) What is CFM load profile in each shift? What is average load in weekday and weekends? 7) Verify CAC chart for each compressor power consumption? 8) Verify current and baseline discharge pressure. 9) Collect compressor nameplate and data sheet. 10) Verify annual energy consumption 385,080kWh. 11) What are the two compressors control method and cooperation sequencing. 12) How is the VFD for one compressor controlled? | (1) Verify that the new tank has been installed and sized at 1550 gal? (2) Check actual CFM load profile? How about baseline? (3) Verify how does the tank size impact the compressors operation? |
| Inspection Findings | 1) Site observations: - One compressor was operating. The discharge air pressure was 102psig. - The tank pressure was between 95psig and 100psig. - Compressor cycling: 15 seconds unloaded; 25 seconds loaded. 2) According to the facility representative: - The leakage was identified and repaired by the company of Browns Compressor Repair using ultrasound detectors. - All the leakage was checked after the repair using ultrasound detectors. - Before the program (two measures): occasionally two compressors running. After the program (two measures): only one compressor needed. - He could not remember the compressor discharge air pressure set point before the program. |  |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | 8,760 | 7,000 | 48,756 | 145,873 | 10 | 10 | 487,560 | 1,458,734 | 8.10 | 0.00 |
| 2 | Re-gear compressors | 8,760 | 7,000 | 42,901 | 16,909 | 15 | 15 | 643,515 | 253,637 | 7.20 | 3.33 |
| Project level |  |  |  | 91,657 | 162,783 |  |  | 1,131,075 | 1,712,371 | 15.30 | 3.33 |

| Nexant Calculations: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EEM 1: | Annual full production operation hours: | 4112 | hrs |  |  |  |  |  |
|  | Annual partial production hours | 2888 | hrs |  |  |  |  |
|  | partial production amount | 0.333 |  |  |  |  |  |
|  | Compressor power consumption | 0.18 | kW/cfm |  |  |  |  |  |
|  | Compressed air repair |  | 112.9 | cfm |  |  |  |  |  |
|  | kWh savings = 112.9cfm x 0.18kw/cfm x (4112 + 2888)hrs = 145,873 kWh |  |  |  |  |
| EEM 2: | Compressor Bhp |  |  |  |  |  |  |  |  |
|  | Discharge pressure before the program | 115 | psig |  |  |  |  |
|  | Discharge pressure after the program | 105 | psig |  |  |  |  |
|  | Current cycling period | 15 | seconds loaded |  |  |  |  |
|  |  | 25 | seconds unloaded |  |  |  |  |
|  | Compressor loaded power | 82.51 | kW |  |  |  |  |  |
|  | Compressor unloaded power | 14.32 | kW |  |  |  |  |  |
|  | hourly power consumption = 82.51 x (15/(15+25)) + 14.32 x (12/(15 +25)) = 39.89 kW |  |  |
|  | Power consumption before the measure implementation | 43.23 | kW |  |  |  |
|  | kWh savings = (43.23 – 39.89)kW x 4112hrs + (43.23 – 39.89)kW x 2888hrs x 0.33 = 16,909kWh |  |  |
|  | kW savings = (43.23 – 39.89) = 3.33 kW |  |  |

Nexant Calculations Summary: Nexant has different kWh energy savings than reported savings because

- The project reported different energy than its calculation results (calculations was 197,275 kWh and 26,995 kWh; reported savings was 48,756 kWh and 42,901 kWh)

- Nexant uses lower annual operating hours

- Nexant calculates power savings by on-site observation of compressor cycling (on/off) instead of estimating by percentage of power consumption as in the project document.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-02-M-004 |
| Facility Business | Metal Manufacturing |
| Building Square Feet | 95,000 |
| Project Completion Date | 11/25/2002 |
| CL&P Annual Energy Savings (kWh) | 85,010.00 |
| CL&P Lifetime Energy Savings (kWh) | 425,050.00 |
| Total Incentives | $1,338 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/9/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Repair compressed air leaks | Upgrade the compressed air system |
| Measure Life (years) | 5 | 10 |
| Total Number of Units | 11 | 1 |
| CL&P-reported annual kWh Savings | 85,010.00 | 15,813.00 |
| Assumptions in CL&P-reported Savings | (1) leakage = 49.8 CFM (2) Annual operation hours: hours | 1) Reduce entire plant pressure from 91psig to 85 psig. |
| Calculation Methodology for CL&P-reported Savings | N/A | N/A |
| Inspection Action Items | 1) Were all 11 leaks (49.8CFM) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load demand profile in the typical daily production? 5) Verify actual compressors hours? 6) Collect complete compressors nameplates 7) Collect all compressors operation data sheet including % power vs. % CFM? 8) What is actual compressor operation pressure? 9) Collect all related compressors control methods. 10) If there is more than one compressor, verify their sequencing schedules. | This measure was not implemented in the report 1) Verify if this measure has been implemented? 2) Airflow demand profile of entire plant? 3) Check if pressure is reduced from 91 psig to 85 psig? 4) Ask how this measure impacts the operation pressure? |
| Inspection Findings | 1. The facility moved from the old site to the current address between sep 2003 and Nov 2003, which is after the completion of this project. 2. After the relocation, the manufacturing layout and system was copied to the current facility. 3. Walk through all 11 leaks, it was found all leaks are either replaced by new connection or new valves. Since only partial production during the visit, some machines are off. Check running machines, no leakage is found. 4. Two compressors are working for the production. The big one operates during Monday to Thursday; the small one runs only on Friday. 5. According to the operator, the big compressor has power 43-48kW during Monday to Thursday; On site test (Friday) showed 35-38kW. | 1. This measure was implemented through project. 2. A loop was added at the end of the piping line, which allowed reducing tank pressure from 90psig to 85psig. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks | N/A | 4,472 | 85,010 | 42,314 | 5 | 5 | 425,050 | 211,570 | N/A | 7.57 |
| 2 | Upgrade the compressed air system | N/A | 4,472 | 15,813 | 10,187 | 10 | 10 | 158,130 | 101,866 | N/A | 2.29 |
| Project level |  |  |  | 100,823 | 52,501 |  |  | 583,180 | 313,437 |  | 9.86 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | 100% production hours | 4056 | hrs |  |  |  |  |  |  |  |
|  | 30% production hours | 416 | hrs |  |  |  |  |  |  |  |  |
|  | Total leakage hours | 4472 | hrs |  |  |  |  |  |  |  |  |
|  | Assume efficiency | 0.19 | kW/cfm |  |  |  |  |  |  |  |  |
|  | Leakage repaired | 49.8 | cfm |  |  |  |  |  |  |  |  |
| EEM 2#: | Big compressor power | 48 | kW |  |  |  |  |  |  |
|  | Small compressor | 44.76 kW | (for 30% production) |  |  |  |  |  |
|  | Pressure change from 90psig to 85psig |  |  |  |  |  |  |  |  |  |
|  | kWh savings = 0.5% x (90-85) x ( 48kW x 4056 + 416 x 44.76) = 10,187 kWh |  |  |  |  |  |

|  | Measure 1 and 2 |  |
| --- | --- | --- |
|  | Existing Equipment |  |
|  | Compressor 1 | Compressor 2 |
| Quantity | 1 | 1 |
| Manufacturer | Sullair | Quincy |
| Type | Rotary Screw | Screw |
| Cooling type | air | air |
| Model | TS20V-200H/A/SUL | QSI-350-ACA3 |
| Ser. | 003-126112 | 204-155-0-9256 |
| HP/BHP | 200 | 75 |
| CFM rating |  |  |
| Pressure (PSIG) | 102-110psi | 102 |
| Fan motor HP (if air cooled) |  |  |
| Control type | VFD | Load/No load |
| Motor Manufacture |  |  |
| Motor model |  |  |
| Motor Eff. |  |  |
| Dryer Manufacturer/model | Motivair/ICE 100 | Motivair/DE 111 |
| Dryer HP | 5.5 kW | 4.4 kW |
| Operating Schedule |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-02-M-011/01 |
| Facility Type | Manufacturing |
| Facility Square Feet | 185,000 |
| Project Completion Date | 12/1/2003 |
| CL&P Annual Energy Savings (kWh) | 65,157 |
| CL&P Lifetime Energy Savings (kWh) | 513,545 |
| Total Incentives | $976 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 5/31/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on this project documents Nexant received from CL&P |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Compressor Sequencing | Repair compressed air leaks | Install a compressed air storage tank |
| Measure Life (years) | 15 | 5 |  |
| Total Number of Units |  | 24 |  |
| CL&P-reported annual kWh Savings | 18,776.00 | 46,381.00 | 102,600.00 |
| Assumptions in CL&P-reported Savings | 1) Sequence is: Curtis 40 HP compressor first; Joy 30HP compressor second; Ingersoll Rand 25 HP compressor as the third | (1) Leakage: Total leakage = 66.7CFM (2) Total Hours =4100 (3) Compressor efficiency = 0.188 kW/cfm | 1) The tank is 1060 gallons. |
| Calculation Methodology for CL&P-reported Savings | N/A | N/A | N/A |
| Inspection Action Items | 1) Check if 3 compressors are operating in sequence? 2) How 3 compressors are sequenced? 3) Verify that proposed sequence is functioning. 4) What is actual production CFM load requirement in different shifts? 5) Verify actual plant operation hours (4100)? 6) Collect complete compressors nameplates and operation data sheet including power consumption at different CFM? | 1) Were all (66.7CFM) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load profile in the typical daily production? 5) Verify actual hours? 6) Check that the Trim Unit is actually off in the production? 7) Collect complete compressors operation data sheet including power consumption at different CFM? 8) What is actual compressor operation pressure? | 1) Ask if this measure has been implemented? How? 2) Ask how this measure impact compressors operation? 3) Collect system pressure in the baseline and EEM? |
| Inspection Findings | 1) The old Curtis compressor has been replaced by a new Ingersoll-Rand compressor 3 month ago. 2) Currently, only the two old compressors operate in sequencing for a line. The new compressor runs independently with VFD control for a separate line. 3) Current plan operation hours 24/7. 4) Site observations: - Among the two old compressors, the old Ingersoll-Rand compressor was operating; 100-70psig - The new Ingersoll-Rand compressor 100psig; 42% capacity 5) According to the staff, mostly the Ingersoll-Rand compressor operates; and occasionally the Joy operates. | 1) 30% of the machines where there were leakage has been removed, which account for 37% of total leakage. 2) No leakage was found by sample check. | 1) Not with this project |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Compressor Sequencing | 4,100 | 8,760 | 18,776 | 34,717 | 15 | 15 | 281,640 | 520,755 | 2.70 | 0.00 |
| 2 | Repair Compressed Air Leaks | 4,100 | 8,760 | 46,381 | 52,644 | 5 | 5 | 231,905 | 263,220 | 6.68 | 7.56 |
| 3 | Add a storage tank |  |  | 102,600 |  |  |  |  |  |  |  |
| Project level |  |  | 65,157 | 87,361 |  |  | 513,545 | 783,974 | 9.38 | 7.56 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM1#: | 30hp Joy and 25hp Ingersoll Rand are sequencing |  |  |  |  |  |
|  | Assume 25% power at no load condition |  |  |  |  |  |
|  | kWh savings = 0.25 x 25hp x 0.7464 x 0.85 x 8760 = 34,717 kWh |  |  |  |  |
| EEM2#: | Assume 37% leaked machines are removed. |  |  |  |  |  |  |  |
|  | Total leakage repaired in the beginning of this program 66.7cfm |  |  |  |  |  |  |
|  | compressor eff. = 0.18 kW/cfm |  |  |  |  |  |  |  |
|  | 3600Hrs in 50% production; 5160Hrs in the 100% production |  |  |  |  |  |  |  |
|  | kWh savings =66.7cfm x (1-0.37) x 0.18kW/cfm x 5160hrs + 66.7cfm x (1-0.37) x 0.18kW/cfm x 3600hrs x 50% = 52,644 kWh |  |
| EEM3#: | Not included in this project |  |  |  |  |  |  |  |  |  |

Nexant Calculations Summary:  project kWh savings increased from 65,157 kWh to 87,361 kWh because

- Nexant uses higher annual operating hours based on the site interview with the facility representative

- Nexant learned that 37% leaked machines had been removed from the site.

Related Equipment Information

| Measure 1 and 2 Existing Equipment Compressor 1 Compressor 2 (Trim unit) Compressor 3 Quantity 1 1 1 Manufacturer Curtis Joy (Twist Air) Ingersoll Rand Type Cooling type air air Model TA-030BA121TH U25HE-SP HP 40 30 25 CFM rating 100 Pressure (PSIG)/actual pre. 125/100-70 Fan motor HP (if air cooled) Control type (Current) N/A load/No load load/No load Control type (previous) load/No load load/No load load/No load Motor Manufacturer Motor Eff. 93.00% Energy rate (kW/cfm) Operating Schedule | New Compressor Quantity 1 Manufacturer Ingersoll-Rand (Nirvana) Type Screw Cooling type Air Cooled Model N50A/C Compressor HP 50 CFM rating Pressure (PSIG)/actual pre. 145/100 Fan motor HP (if air cooled) 3.2 Control type (Current) N/A Control type (previous) VFD Motor Manufacturer Motor Eff. Dryer Model ZEKS/300HSGA400 Dryer HP 2 Energy rate (kW/cfm) |
| --- | --- |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-00-M-020 |
| Building Type | Office |
| Building Square Feet | 75,000 |
| Project Completion Date | 3/18/2002 |
| CL&P Annual Energy Savings (kWh) | 49,061.00 |
| CL&P Lifetime Energy Savings (kWh) | 490,610.00 |
| Total Incentives | $7,632 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 7/13/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Efficient lighting fixture replacement on the 3rd floor main lobby | Add occupancy sensors | Air Balancing of the 3rd floor VAV |
| Measure Life (years) | 15 | 10 | 10 or 15? |
| Total Number of Units | 14 | 126 |  |
| CL&P-reported annual kWh Savings | 959.7 | 4631 | 49,061.00 |
| Assumptions in CL&P-reported Savings | 1) 14 old fixtures =1.07 kW. 2) 14 New lighting =0.79 kW. 3) Hours = ; | 1) 126 fixtures = kW. 2) Hours = ; | 1) Total hours = 1750; 2) IGV operation replace CAV operation. 3) Supply and return fan power is 30 HP and 10 HP respectively. 4) There is electricity reheat on the 3rd floor box. 5) Bin data is used. |
| Calculation Methodology for CL&P-reported Savings | Demand savings = 1.07 - 0.79 = 0.27kW kWh savings = 0.27 x 3554 = 959.7 kWh |  | Fan power savings = CAV supply and return fan power - supply and return fan power with Inlet guide vane installation Total savings = Fan power savings + Electricity reheat savings. |
| Inspection Action Items | 1) Verify if this measure has been implemented or not? 2) Check the original and new lighting fixture power. 3) Check annual lighting hours? | 1) Verify if this measure has been implemented or not? How many have been installed? 2) What are total hours of occupancy? 3) Check lighting fixture types. | 1) Verify exactly what action is taken for this implementation? 2) What were the problems before for this floor? 3) What type of building shape? 4) What is minimum air flow if VAV boxes were installed? (10% - 15% in the report) 5) Verify AHUs operating hours. 6) Check the AHU airflow capacity. |
| Inspection Findings | 1) According to the facility representative, this measure is being implemented. 2) On site observations: there 14x2 T12 lighting fixtures in the lobby of 3rd floor. | 1) According to the facility representative, this measure was not implemented. | 1) This measure has been implemented. |

| Measure # | 4 | 5 | 6 |
| --- | --- | --- | --- |
| Measure Description | Retrofit inlet guide vanes with VFDs | Fix economizer damper for 3rd floor AHU | Shut down hot water pump when unoccupied |
| Measure Life (years) | 15 | 15 | 10 |
| Total Number of Units | 2 | 1 | 1 |
| CL&P-reported annual kWh Savings | 83,091.00 | 10,925.00 | 1,259.00 |
| Assumptions in CL&P-reported Savings | 1) Total hours = 3500; 2) Supply and return fan power is 30 HP and 10 HP respectively. | 1) HVAC end use = 72833 kWh; 2) Savings =15% | 1) Hot Water pump = 0.288 kW; 2) Hours =4380 hrs. |
| Calculation Methodology for CL&P-reported Savings |  | Savings =15% x 72833 kWh = 10925 kWh | Savings = 0.288 x 4380 hrs = 1261 kWh |
| Inspection Action Items | 1) Verify if VFD have been installed and are operating? 2) Check static pressure set points? 3) Check occupancy hours of the area served by AHUs? | 1) Check if the economizer damper has been fixed and is working as desired? 2) Ask if economizer is always used in the winter? 3) Ask how economizer damper performed before the implementation? 4) Collect this AHU fan power and airflow capacity. 5) What are the operation hours of this AHU? | 1) Check if the hot water pump is controlled off when it is unoccupied? 2) Collect this pump nameplate. 3) Ask if the water system enable hours per year. What the water system is for? |
| Inspection Findings | 1) According to the facility representative, this measure was not implemented. | 1) This measure has been implemented. | 1) According to the facility representative, this measure was not implemented. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Efficient lighting fixture replacement on the 3rd floor main lobby |  |  | 960 |  | 15 | 15 | 14,396 |  |  |  |
| 2 | Add occupancy sensors |  |  | 4,631 |  | 10 | 10 | 46,310 |  |  |  |
| 3 | Air Balancing of the 3rd floor VAV |  | 3,484 | 49,061 | 29,804 | 10 | 10 | 490,610 | 298,043 |  | 0 |
| 4 | Retrofit inlet guide vane with VFD |  |  | 83,091 |  | 15 | 15 | 1,246,365 |  |  |  |
| 5 | Fix economizer damper for 3rd floor AHU |  | 3,484 | 10,925 | 10,125 | 15 | 15 | 163,875 | 151,875 |  | 0 |
| 6 | Shut down hot water pump when unoccupied |  |  | 1,259 |  | 10 | 10 | 12,590 | 0 |  |  |
| Project level |  |  |  | 149,927 | 39,929 |  |  | 1,974,146 | 449,918 |  | 0.00 |

| 1,2,4,6 | Measures that was not implemented in the reported savings and database |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 3: | AHU annual operating hours |  |  | 3484 | hrs |  |  |  |  |  |  |
|  | Assumed unoccupied summer hours |  | 791 | hrs |  |  |  |  |  |  |
|  | Assume 200 x 125 ft2/floor, 15feet high/floor |  |  |  |  |  |  |  |  |  |
|  | RTU efficiency in the summer |  |  | 1.2 | kW/ton |  |  |  |  |  |  |
|  | cooling savings due to the night set back (estimated by envelope heat transfer for different room temperature) |  |  | 8.125 | Tons |  |  |  |  |  |  |
|  | kWh Savings by fixing night time set back = 1.2 kW/ton x 8.125 ton x 791 hrs = 7712.25 kWh |  |  |  |  |  |
|  | Supply fan |  |  | 30 | hp |  |  |  |  |  |  |
|  | Return fan |  |  | 10 | hp |  |  |  |  |  |  |
|  | Assume average VAV energy consumption percentage | 50% |  |  |  |  |  |  |  |
|  | cooling operating hours |  |  | 1742 | hrs |  |  |  |  |  |  |
|  | kWh savings due to fixing VAV system = (30+10)hp x 0.746 kw/hp x 0.85 x (1-50%) x 1742 hrs = 22092 kWh |
|  | Total kWh savings = 22,092 + 7712 = 29,804 kWh |  |  |  |  |  |  |  |  |  |  |
| EEM 5: | winter hours |  |  | 1000 | hrs |  |  |  |  |  |  |
|  | Assumed airflow rate for the third floor AHU in the winter | 12500 | cfm |  |  |  |  |  |  |
|  | cooling load with failed economizer |  | 16.875 | ton |  |  |  |  |  |  |
|  | assumed RTU efficiency in cold weather |  | 0.6 | kW/ton |  |  |  |  |  |  |
|  | the winter energy consumption by failed economizer in the occupied mode = 16.875ton x 0.6kw/ton x 1000hrs = 10,125 kWh |  |  |

Related Equipment Information:

|  | Measure 1 |
| --- | --- |
|  | Existing Equipment |
|  | 3rd floor AHU |
| Quantity | 1 |
| Manufacturer | Trane |
| System Type | Single Duct VAV with Ele. Reheat |
| Model/Ser. | SFHCC754LH66C99D3A01BENRTY8/J89A 74403 |
| Fan HP | SF: 30 hp; EF: 10 hp |
| Tons | 75 |
| CFM |  |
| Motor Eff. |  |
| Control type |  |
| Min. box setting (%) | 30615(by design); 20576 (actual) |
| Operating Schedule | 6:00 - 18:00 M-F; 6:00 - 13:00 Sat |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-02-M-007 |
| Facility Business | Manufacturing |
| Building Square Feet | >200,000 |
| Project Completion Date | 6/20/2003 |
| CL&P Annual Energy Savings (kWh) | 45,406 |
| CL&P Lifetime Energy Savings (kWh) | 90,812 |
| Total Incentives | $3,116 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/10/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Clean condenser unit coils |
| Measure Life (years) | 2 |
| Total Number of Units | 52 |
| CL&P-reported Annual kWh Savings | 45,406.00 |
| Assumptions in CL&P-reported Savings |  |
| Calculation Methodology for CL&P-reported Savings |  |
| Inspection Action Items | 1) Check the coils are clean. 2) Ask how often the coils are cleaned. 3) Ask how the clean impact power consumption? 4) Collect compressors or other equipment power which are related with the coil clean? 5) Check how many coils and their sizes? 6) Check what these coils are used for? |
| Inspection Findings | 1. The coils could not be identified since the current facility manager was joined this facility after this program. 2. Nexant assumes the same savings as reported since there is no enough information to be used for evaluation. |

| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks |  |  | 45,406 | 45,406 | 2 | 2 | 90,812 | 90,812 | 31.10 | 0.00 |
| Project level |  |  |  | 45,406 | 45,406 |  |  | 90,812 | 90,812 |  | 0.00 |

Related Equipment Information

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  | Existing Equipment |  |  |
|  | Compressor 1 (Main Compressor) | Compressor 2 (Backup) | Compressor 3 |
| Quantity | 1 | 1 | 1 |
| Manufacturer | Le ROI Dresser | Ingersoll Rand | Kaeser |
| Type | Rotary Screw | Rotary Screw | Rotary Screw |
| Cooling type | Air cooled | Air cooled | Air cooled |
| Model/Ser. | WE75 SS II | SSR-EP50SE/G3867U95233 | BS61/510272 |
| HP | 75 | 50 | 50 |
| CFM rating |  | 194 scfm | 240scfm |
| Pressure (PSIG) | 109psig monitored | 125 psig | 110 psig (102-112psig) |
| Fan motor HP (if air cooled) | 3 | 3 | 3 |
| Control type | Load/no load |  |  |
| Motor Eff. | 92.3% |  |  |
| Dryer Model | Le ROI / LR 300 |  |  |
| Dryer power (hp) | 1.5 | 1.0 | 1.5 |
| Dryer airflow rate | 300 scfm@100 psig & 100F (Refrigerant R-12) |  | R-12 |
| Energy rate (kW/cfm) | 0.207222222 | 0.213631157 | 0.172685185 |
| Operating Schedule |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-03-M-001 |
| Facility Type | Manufacturing |
| Building Square Feet | 151,553 |
| Project Completion Date | 4/14/2003 |
| CL&P Annual Energy Savings (kWh) | 42,661.00 |
| CL&P Lifetime Energy Savings (kWh) | 639,915.00 |
| Total Incentives | $4,456 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 5/25/2006 |
| Inspected By: | Dakers, Yujie |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Design, furnish and install drain all traps |
| Measure Life (years) | 15 |
| Total Number of Units | 12 |
| CL&P-reported kWh Savings | 42,661.00 |
| Assumptions in CL&P-reported Savings | N/A |
| Calculation Methodology for CL&P-reported Savings | N/A |
| Inspection Action Items | 1) What was the old drain diameter? 2) Check if old timer drains had timing ___ seconds on and ___ minutes off? 3) Inspect each drain to verify its existence. 4) What should be actual coefficient of flow? 5) Collect all related compressors nameplates 6) Collect all related compressors control methods and sequencing if more than one compressor provide air to the plant. 7) Collect all related compressors operation data (% kW vs. % cfm). 8) Actual compressor CFM load profile? |
| Inspection Findings | (1) A new compressor was added in 11/2002; It was operating 64% capacity and 110psi based on the site observations. (2) 11 drains were found on site |

|  |  | Annual Electricity Savings |  |  |
| --- | --- | --- | --- | --- |
| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | No-Loss Drains | N/A | 8,760 | 42,661 | 6,721 | 15 | 15 | 131,400 | 100,817 | N/A | 0.00 |
| Project level |  |  | 8,760 |  | 6,721 |  |  |  | 100,817 | N/A | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| Assumption: | Old drain 5 minutes per day |  |  |  |  |  |  |  |  |  |
|  | Drain size | 1/2" |  |  |  |  |  |  |  |  |
|  | System pressure | 90psig |  |  |  |  |  |  |  |  |
|  | Standard orifice leakage rate at 90psig and ½” = 279cfm |  |  |  |  |  |  |  |
|  | Flow coefficient = 0.4 |  |  |  |  |  |  |  |
|  | Compressor operating efficiency = 0.18 kW/cfm |  |  |  |  |  |  |  |
|  | kWh savings = (279cfm x11)x 300sec./(60*24*60)sec. x 0.4 x 0.18 x 8760 = 6,721kWh |  |  |  |  |  |

Related Equipment Information:

|  | Measure 1 |  |
| --- | --- | --- |
|  | New Equipment |  |
|  | Compressor 1 |  |
| Quantity |  |  |
| Manufacturer | Ingersoll-Rand |  |
| Type | Screw |  |
| Cooling type | air cooled |  |
| Model | IRN100H-CC |  |
| BHP/kW | 100hp compressor/5hp fan |  |
| CFM rating | 138-413 |  |
| Pressure (PSIG) / actual | 145/110 |  |
| Control type | VFD |  |
| Mechanical Eff. |  |  |
| Energy rate (kW/cfm) |  |  |
| Operating Schedule |  |  |

| New Equipment |  |  |  |  |
| --- | --- | --- | --- | --- |
| Drain Traps | Installed? Yes/No | Pressure | Size | Model |
| 1 | Yes | 90 | 1/2" |  |
| 2 | Yes | 90 | 1/2" |  |
| 3 | Yes | 90 | 1/2" |  |
| 4 | Yes | 90 | 1/2" |  |
| 5 | Yes | 90 | 1/2" |  |
| 6 | Yes | 90 | 1/2" |  |
| 7 | Yes | 90 | 1/2" |  |
| 8 | Yes | 90 | 1/2" |  |
| 9 | Yes | 90 | 1/2" |  |
| 10 | Yes | 90 | 1/2" |  |
| 11 | Yes | 90 | 1/2" | Drain All/1700 |
| 12 | No |  |  |  |
| Program Name | CL&P O&M Program |
| Project Number | WE-02-M-009 |
| Facility Type | OEM Manufacturing |
| Building Square Feet |  |
| Project Completion Date | 9/17/2002 |
| CL&P Annual Energy Savings (kWh) | 21,559.00 |
| CL&P Lifetime Energy Savings (kWh) | 323,385.00 |
| Total Incentives | 2,931.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/13/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Add a small compressor w/Air Dryer & Filter Set |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported kWh Savings | 21,559.00 |
| Assumptions in CL&P-reported Savings | N/A |
| Calculation Methodology for CL&P-reported Savings | N/A |
| Inspection Action Items | 1) Check the 5 hp compressor set has been installed and are operating as intended. 2) Collect data sheet for the small new 5hp compressor including power efficiency vs. % cfm. 3) Collect data sheet for the existing big 30hp compressor including efficiency and control method. 4) Collect airflow demand on the weekends for the wire machine. 5) What is the new machine operation hour on the weekends? 6) Collect real power for the new and existing compressors. 7) Complete nameplates for both the new and existing compressors. 8) Collect control methods of the two compressors. 9) How does this measure benefit savings? |
| Inspection Findings | 1. The small compressor has been installed to provide compressed air for a special machine (wiring machine) after 11:00pm Monday to Friday. The wiring machine is served by the main compressor during the daytime operation. According to the operator, the wiring machine needs 2.0 cfm. 2. Site observations of the new small compressor: Off; total operating hours are 280hours since its installation. 3. Site observations of the main compressor: ON; VFD: 42Hz (33% power) ~ 54Hz; total 26,150 hours and 10,853MWh Compressor: 33% load to 54% load; 4. Maintenance log of the main compressor: 12,356 hours between 6/11/2003 to 5/31/2006 |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Add a small compressor w/Air Dryer & Filter Set |  | 2,080 | 21,559 | 12,139 | 15 | 15 | 323,385 | 182,079 | 0.00 | 0.00 |
| Project level |  |  |  | 21,559 | 12,139 |  |  | 323,385 | 182,079 | 0.00 | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1# | Small compressor: | Annual full load hours = 74 hrs |  |  |  |  |  |  |
|  |  | full load power | 3.73 | kW |  |  |  |  |  |  |
|  | Small compressor kWh | = 74 hrs x 3.73 kW = 276 kWh |  |  |  |  |  |  |  |
|  | Main compressor: | Annual production hours between 11:00pm and 7:00am = 2080 hrs |  |  |
|  |  | Full load power = 29.84 kW |  |  |  |  |  |  |
|  |  | Minimum power percentage 20% |  |  |  |  |  |

Main compressor kWh = 2080 hrs x 29.84 kW x 20% = 12,397 kWh

Annual kWh savings = Main compressor kWh - Small Compressor kWh = 12,139 kWh

Related Equipment Information

|  | Measure 1 |  |  |
| --- | --- | --- | --- |
|  | Existing Equipment | New Equipment |  |
|  | Compressor 1 | Compressor 2 | Dryer |
| Quantity | 1 | 1 | 1 |
| Manufacturer | Garden Denver | Quincy | Motivair |
| Type | Rotary screw | reciprocating |  |
| Cooling type | Air cooled | Air cooled |  |
| Model | VS 170 (304EGC753) | 150925-133 (325) | DE 107 |
| HP | 40 | 5 |  |
| CFM rating | 170 |  |  |
| Pressure (PSIG) | 100 | 110 |  |
| Control type | VFD | cycle on/off | cycle |
| Mechanical Eff. |  | 82.50% |  |
| Energy rate (kW/cfm) |  |  |  |
| Operating Schedule |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-02-M-016 |
| Facility Business | Grocery Store |
| Building Square Feet | 95,000 |
| Project Completion Date | 5/7/2003 |
| CL&P Annual Energy Savings (kWh) | 10,500.00 |
| CL&P Lifetime Energy Savings (kWh) | 241,500.00 |
| Total Incentives | $4,480 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 9/6/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # |  | 1 |
| --- | --- | --- |
| Measure Description | Meat Room Evaporator Unit | Add high speed door 28 degree room |
| Measure Life (years) |  | 23 |
| Total Number of Units |  | 1 |
| CL&P-reported kWh Savings |  | 10,500.00 |
| Assumptions in CL&P-reported Savings |  |  |
| Calculation Methodology for CL&P-reported Savings |  |  |
| Inspection Action Items | 1) Check if this measure has been implemented? 2) Check that the high speed door has been installed and operate as intended? 3) Collect operation data for the 4 new units and old units including efficiency data. | 1) Check that new equipment has been installed and are operating as intended? 2) Ask how this measure impact kW consumption. 3) Collect the nameplates for the new and old units, especially power capacity and efficiency data. |
| Inspection Findings | 1) This measure belong to the project WE02M003 | 1) This measure has been implemented. 2) According to Paul: - The old door was rubber door; the new door is half-plastic and half rubber. - The new door opens faster. - The new door seal tightly. 3) On-site observations: - The door size was estimated to be 10' x 9' |

| WE-02-M-016 Savings Summary |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
|  |  |  |  | Savings (kWh) | Savings (kWh) | Lifetime (yrs) |  | Savings (kWh) | Savings (kWh) | Savings (kW) | Savings (kW) |
| 1 | Add high speed door 28 degree room |  | 8,760 | 10,500 | 7,450 | 23 | 23 | 241,500 | 171,359 | 1.52 | 0.41 |
| Project level |  |  |  | 10,500 | 7,450 |  |  | 241,500 | 171,359 |  | 0.41 |
| Nexant calculations |  |  |  |  |  |  |  |  |  |  |
| EEM1# | The door size | 10 x 9 | FEET |  |  |  |  |  |  |  |  |
|  | Assumptions: |  |  |  |  |  |  |  |  |  |  |
|  | the old door left open for 5 minutes longer than the new door and 10 times a day |  |  |  |
|  | average air velocity | 1 | ft/sec |  |  |  |  |  |  |  |  |
|  | air density | 0.075 | lb/ft3 |  |  |  |  |  |  |  |  |
|  | room air temperature | 70 | F |  |  |  |  |  |  |  |  |
|  | average cooler temperature | 28 | F |  |  |  |  |  |  |  |  |
|  | assumed new unit cooling efficiency (air cooled) = 1.2 kW/ton |  |  |  |  |  |  |

Nexant Calculations Summary:  Nexant uses site inspection results to calculate savings combined with assumption.

Calculation methodology:

General heat loss due to infiltration = air density x leakage flow rate x (inner space temperature – outer temperature)

kWh savings = Chiller kW/ton x heat loss (tons) x annual operating hours

kW savings = Chiller kW/ton x heat loss (tons)

| WE-02-M-016 Related Equipment |  |  |  |
| --- | --- | --- | --- |
| The new refrigeration system that serve the measures |  |  |  |
| total tonnage (ton) |  | 265 |  | tons |
| compressors with 15F suction temperature (F) | 60 | 75 | hps |
| compressors with -22F suction temperature (F) | 20 | 25 | hps |
| compressors with -35F suction temperature (F) | 7.5 |  | hps |
| refrigerant | R-22 |  |  |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-01-M-034 |
| Building Type | Grocery Store |
| Building Square Feet |  |
| Project Completion Date | 11/23/2001 |
| CL&P Annual Energy Savings (kWh) | 164,664 |
| CL&P Lifetime Energy Savings (kWh) | 2,469,960 |
| Total Incentives | $37,169 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 6/26/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Parasense monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 164,664.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. |
| Calculation Methodology for CL&P-reported Savings | Annual electricity consumption in billing history with total of 3,293,280 kWh Annual savings = 3,293,280 x 5% = 164,664 kWh |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |
| Inspection Findings | 1) There are two Parasense monitoring panels, one with 15 electric panels monitored and another one with 4 electric panels monitored. 2) The two monitoring panels record major power consumption of this facility including 2 refrigeration rack system, RTUs, Lighting panels, and exhaust system and so on. 3) The kW power is recorded every 30 minutes and can be shown in graphic. Technicians check the kW history and identify problems periodically. Then fix the problems if there are. 4) According to the store technician - he came to this store every two weeks to check the system - The problem frequency is from once every 6 month (low side) to once every 2 months (high side) - The biggest problem in this store since this program: 5 condensing fans (1/2 hp each) were locked on when they supposed to be off sue to relay failure. - The small problems are like lighting: for example, lights 20-100 amps with 277 volts power were found on at night when they supposed to be off. 5) Site observations: - Two compressors were on for each rack refrigeration system. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Parasense monitoring system |  |  | 164,664 | 31,880 | 15 | 15 | 2,469,960 | 478,196 | 0.00 | 0.00 |
| Project level |  |  |  | 164,664 | 31,880 |  |  | 2,469,960 | 478,196 | 0.00 | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | Nexant assumed the most worse case with |  |  |  |  |  |  |  |  |
|  | 1. highest problem happening frequency |  |  |  |  |  |  |  |  |
|  | 2. biggest power consumption for each case |  |  |  |  |  |  |  |  |
|  | 3. all problems happened at the same time |  |  |  |  |  |  |  |  |
|  | technician check the monitoring system every 2 weeks = 14 days |  |  |  |  |  |
|  | Problem frequency (most conservative estimation) 6 times a year |  |  |  |  |  |  |
|  | problem 1#: | 5 condensing fans were locked on in the winter | 1.8625 | kW |  |  |  |  |
|  | Problem 2#: | Lights were locked on 20-100 Amps and 277 volts |  |  |  |
|  |  | Power factor |  |  | 0.95 |  |  |  |  |  |
|  |  | Power = 45.57758 kW |  |  |  |  |  |  |  |  |
|  | Store close hours 11:00 pm to 7:00am = | 8 hours at night |  |  |  |  |  |
|  | Annual kWh savings = (1.86 + 45.6) kW x 8 x 14 x 6 = 31,880 kWh |  |  |  |  |  |  |

Nexant Calculation Summary:

Project kWh savings reduced from 164,664 kWh to 31,880 kWh because Nexant calculates savings based on the site interview with the store technician to identify all the problems happened since the installation of the monitoring system.  The project document estimated the savings by 5 % of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-01-M-018 |
| Building Type | Grocery store |
| Building Square Feet |  |
| Project Completion Date | 12/20/2001 |
| CL&P Annual Energy Savings (kWh) | 151,814 |
| CL&P Lifetime Energy Savings (kWh) | 2,277,210 |
| Total Incentives | $27,178 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 7/6/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Install energy monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 151,814.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. (Northeast Utility performed an audit showed 8% savings were actually realized) |
| Calculation Methodology for CL&P-reported Savings | Annual electricity consumption in billing history with total of 3036288 kWh 1) Meter 1: 1598208 kWh 2) Meter 2: 1438080 kWh |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |
| Inspection Findings | 1) There are two Parasense monitoring panels, one with 15 electric panels monitored and another one with 4 electric panels monitored. 2) The two monitoring panels record major power consumption of this facility including 2 refrigeration rack system, RTUs, Lighting panels, and exhaust system and so on. 3) The kW power is recorded every 30 minutes and can be shown in graphic. Technicians check the kW history and identify problems periodically. Then fix the problems if there are. 4) According to the technician - there were no problems in this store since the installation of this monitoring system as far as he knew. - There is no facility expansion, cutbacks after the completion of this project - this store is to be downsized in the future. - Most of the stores will have a lighting retrofit. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Install energy monitoring system |  |  | 151,814 | 0.00 | 15 | 15 | 2,277,216 | 0.00 | 0.00 | 0.00 |
| Project level |  |  |  | 151,814 | 0.00 |  |  | 2,277,216 | 0.00 | 0.00 | 0.00 |

Nexant Calculation Summary:

Project kWh savings reduced from 151,814kWh to 0 kWh because Nexant calculate savings based on the site interview with the store technician that there was no any problems since the installation of this monitoring system.  The project document estimates the savings by 5 % of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-01-M-032 |
| Building Type | Grocery Store |
| Building Square Feet |  |
| Project Completion Date | 11/23/2001 |
| CL&P Annual Energy Savings (kWh) | 110,430 |
| CL&P Lifetime Energy Savings (kWh) | 1,656,450 |
| Total Incentives | $28,970 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 7/11/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Install energy monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 110,430.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. |
| Calculation Methodology for CL&P-reported Savings | Annual electricity consumption in billing history with total of 2,208,600 kWh Annual savings = 2,208,600 x 5% = 110,430 kWh |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. 4) Verify the measures: - (3) Smart - E monitors Model 7000 - (1) Orakle Data Switch/Weather station |
| Inspection Findings | 1) There are two Parasense monitoring panels, each with 15 electric panels monitored. 2) The two monitoring panel’s record major power consumption of this facility including refrigeration rack system, RTUs, Lighting panels, and exhaust system and so on. 3) The kW power is recorded every 30 minutes and can be shown in graphic. Technicians check the kW history and identify problems periodically. Then fix the problems if there are. 4) According to the store technician - there is no facility expansion, cutbacks after the completion of this project - he came to this store every two weeks to check the system. - There are 1 to 3 issues every year. - The biggest issue in this store since this program: lighting panels were on at night when they supposed to be off. The current is no more than 100amps with 277 volts. - The small issue: VFD was once by-pass. - Each issue was identified in less than 2 -3 weeks. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Install energy monitoring system |  |  | 110,430 | 46,023 | 15 | 15 | 1,656,450 | 690,341 |  | 0.00 |
| Project leve |  |  | 110,430 | 46,023 |  |  | 1,656,450 | 690,341 | 0.00 | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | Nexant assumed the most worse case with |  |  |  |  |  |  |  |  |  |
|  | 1. highest problem happening frequency |  |  |  |  |  |  |  |  |  |
|  | 2. biggest power consumption for each case |  |  |  |  |  |  |  |  |  |
|  | 3. all problems happened at the same time |  |  |  |  |  |  |  |  |  |
|  | technician check the monitoring system every 3 weeks = 21 days |  |  |  |  |  |
|  | Problem frequency (most conservative estimation) 3 times a year |  |  |  |  |  |  |
|  | problem 1#: | VFD was by-passed | 26.00 | kW |  |  |  |  |  |  |
|  | Problem 2#: | Lights were locked on 100 Amps and 277 volts |  |  |  |  |  |  |
|  |  | Power factor = 0.95 |  |  |  |  |  |  |  |  |
|  |  | Power | 26.315 | kW |  |  |  |  |  |  |  |
|  | Store closing hours 11:00 pm to 7:00am = 8 Hrs at night |  |  |  |
|  | Annual kWh savings = 26.315 kW x 21days x 8hrs/day x 3 times+ (26.0 kW x 8 hrs/day+ (0.75) x 26.00 kW x (24 - 8)hrs) x 3times x 21 days= 46,023 kWh |

Nexant Calculation Summary:

Project kWh savings reduced from 110,430 kWh to 46,023 kWh because Nexant calculates savings based on the site interview with the store technician to identify all the problems happened since the installation of the monitoring system.  The project document estimated the savings by 5 % of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-01-M-009 |
| Building Type | Grocery Store |
| Building Square Feet |  |
| Project Completion Date | 12/6/2001 |
| CL&P Annual Energy Savings (kWh) | 121,555 |
| CL&P Lifetime Energy Savings (kWh) | 1,823,335 |
| Total Incentives | $26,972 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/11/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Installation of Parasense monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 121,555.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. |
| Calculation Methodology for CL&P-reported Savings | Annual electricity consumption in billing history with total of 2431104 kWh Annual savings = 2,431,104 x 5% =121,555 kWh |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |
| Inspection Findings | 1) There are two Parasense monitoring panels. 2) The two monitoring panels record major power consumption of this facility including 2 refrigeration rack systems, RTUs, Lighting panels, and exhaust system and so on. 3) The kW power is recorded every 30 minutes and can be shown in graphic. Technicians check the kW history and identify problems periodically. Then fix the problems if there are. 4) According to the store technician - He came to this store often sine his home is in this town. - The problem frequency is once a year at most. - The typical problems are lighting problem. Up to 60 amps with 277 volts power were found on when they supposed to be off. |

| Measure | Measure | Annual Electricity Consumption (kWh) | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Parasense monitoring system | 2,431,104 |  | 121,555 | 3,063 | 15 | 15 | 1,823,328 | 45,942 |  | 0.00 |
| Project level |  |  |  | 121,555 | 3,063 |  |  | 1,823,328 | 45,942 |  | 0.00 |

| Nexant Calculations: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| EEM 1#: | Nexant assumed the worse case is lighting problem that occurred for two weeks. |  |
|  | The technician check the monitoring system every 2 weeks = 14 days |  |
|  | Problem frequency (most conservative estimation) 1 times a year according to the store technician |
|  | Problem 1#: | Lights were locked on 60 Amps and 277 volts |  |  |
|  |  | Power factor 0.95 |  |
|  |  | Power of these lighting = 27.3465 kW |
|  |  | Store close hours 11:00 pm to 7:00am 8 Hrs at night |
|  | Annual kWh savings = (27.3465) kW x 8 hrs/day x 14 days x 1time = 3,063 kWh |

Nexant Calculation Summary:

Project kWh savings reduced from 121,555 kWh to 3,063 kWh because Nexant calculate savings based on the site interview with the store technician to identify all the problems happened since the installation of the monitoring system.  The project document estimates the savings by 5% of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-01-M-010 |
| Building Type | Grocery Store |
| Building Square Feet |  |
| Project Completion Date | 12/6/2001 |
| CL&P Annual Energy Savings (kWh) | 117,350 |
| CL&P Lifetime Energy Savings (kWh) | 1,760,260 |
| Total Incentives | $26,145 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/11/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Installation of Parasense monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 117,350.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. |
| Calculation Methodology for CL&P-reported Savings | Annual electricity consumption in billing history with total of 2347008 kWh Annual savings = 2,347,008 x 5% =117,350.40 kWh |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |
| Inspection Findings | 1) According to the store technician, the two Parasense monitoring panels have been removed since Feb 2006 and replaced by a new monitoring system EG controls. |

| Measure | Measure | Annual Electricity Consumption (kWh) | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Parasense monitoring system | 2,347,008 |  | 117,350 | 0.00 | 15 | 15 | 1,760,256 | 0.00 |  | 0.00 |
| Project level |  |  |  | 117,350 | 0.00 |  |  | 1,760,256 | 0.00 |  | 0.00 |

Nexant Calculation Summary:

Project kWh savings reduced from 117,350 kWh to 0.00 kWh because Nexant calculate savings based on the site interview with the store technician.  This monitoring system generates 0 kWh savings due to its removal.  The project document estimates the savings by 5% of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | EA-01-M-012 |
| Building Type | Grocery store |
| Building Square Feet |  |
| Project Completion Date |  |
| CL&P Annual Energy Savings (kWh) |  |
| CL&P Lifetime Energy Savings (kWh) |  |
| Total Incentives |  |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/10/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Install energy monitoring system |
| Measure Life (years) | 15 |
| Total Number of Units | 1 |
| CL&P-reported Annual kWh Savings | 151,814.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. (Northeast Utility performed an audit showed 8% savings were actually realized) |
| Calculation Methodology for CL&P-reported Savings |  |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |
| Inspection Findings | 1) There are two Parasense monitoring panels. 2) The two monitoring panels record major power consumption of this facility including 2 refrigeration rack system, RTUs, Lighting panels, and exhaust system and so on. 3) The kW power is recorded every 30 minutes and can be shown in graphic. Technicians check the kW history and identify problems periodically. Then fix the problems if there are. 4) According to the technician Brian - he came to this store every 2 weeks. - The problem frequency is once a year at most. - The typical problems are lighting problem. Up to 100 amps with 120 volts power were found on when they supposed to be off. |

| Measure | Measure | Annual Electricity Consumption (kWh) | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Install energy monitoring system | 3,036,288 |  | 151,814 | 2211 | 15 | 15 | 2,277,216 | 33,171 |  | 0.00 |
| Project level |  |  |  | 151,814 | 2,211 |  |  | 2,277,216 | 33,171 |  | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM 1#: | Nexant assumed the worse case is lighting problem that occurred for two weeks. |  |  |  |  |  |  |
|  | technician check the monitoring system every 2 weeks = 14 days |  |  |  |  |
|  | Problem frequency (most conservative estimation) 1 times a year |  |  |  |  |  |
|  | Problem 1#: | Lights were locked on 100 Amps and 120 volts |  |  |  |  |
|  |  | Power factor = 0.95 |  |  |  |  |
|  |  | Lighting power = 19.7448 kW |  |  |  |  |
|  |  | Store close hours 11:00 pm to 7:00am =8 Hrs at night |  |  |  |  |
|  | kW savings = 19.7kW x 8hrs/day x 14days x 1times/year = 2211 kWh |

Nexant Calculation Summary:

Project kWh savings reduced from 151,814 kWh to 2,211 kWh because Nexant calculate savings based on the site interview with the store technician to identify all the problems happened since the installation of the monitoring system.  The project document estimates the savings by 5% of annual store electricity consumption.

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-01-M-027/1 |
| Facility Business | Manufacturing |
| Building Square Feet |  |
| Project Completion Date | 11/13/2001 |
| CL&P Annual Energy Savings (kWh) | 12,000.00 |
| CL&P Lifetime Energy Savings (kWh) | 60,000.00 |
| Total Incentives | $1,320 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/23/2006 |
| Inspected By: | Yujie Cui |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | Repair compressed air leaks |
| Measure Life (years) | 5 |
| Total Number of Units | 12 |
| CL&P-reported annual kWh Savings | 12,000.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = CFM (2) Baseline airflow = CFM; (3) Annual operation hours: hours |
| Calculation Methodology for CL&P-reported Savings | BASE LINE energy: Compressor: EEM1# energy: Airflow = - = CFM kWh savings = Base line - EEM 1# |
| Inspection Action Items | 1) Ask total CFM of all 12 leaks ( CFM) repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load? 5) Verify actual compressor hours? 6) Collect compressors nameplates. 7) Collect each compressor control method and sequencing schedule if there is more than one compressor. 8) Collect complete compressor operation data sheet including power consumption at different CFM? No load power? 9) What is typical compressor operation pressure? |
| Inspection Findings | 1) No leakage was found by sampling. 2) The facility's compressor was outside for repairing and a temporally leased compressor was on service. 3) There is a compressed air tank, which has pressure set point. |

| WE-01-M-027 Savings Summary |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure | Measure | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (years) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| No. | Description | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Repair Compressed Air Leaks |  | 8,424 | 12,000 | 20,218 | 5 | 5 | 60,000 | 101,088 |  | 0.00 |
| Project level |  |  |  | 12,000 | 20,218 |  |  | 60,000 | 101,088 |  | 0.00 |
| Nexant Calculations |  |  |  |  |  |  |  |  |  |  |
| EEM 1# | Annual leakage hours | 8,424 | hrs |  |  |  |  |  |  |  |  |
|  | Assumed air leakage rate | 12 | cfm |  |  |  |  |  |  |  |  |
|  | Compressor operating efficiency | 0.2 | kW/cfm |  |  |  |  |  |  |  |  |

| WE-01-M-027 Related Equipment List |
| --- |
|  | Measure 1 |
|  | Existing Equipment |
|  | Compressor 1 |
| Quantity | 1 |
| Manufacturer | Champion Air Compressor |
| Type | Screw |
| Cooling type | Air cooled |
| Model/Serial | EBA99A/S039736 |
| HP/BHP | 15 |
| CFM rating |  |
| Pressure (PSIG) | 100 |
| Fan motor HP (if air cooled) |  |
| Control type | Load/unload |
| Motor Eff. |  |
| Energy rate (kW/cfm) |  |
| Operating Schedule |  |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-01-M-019 |
| Building Type | Grocery Store |
| Building Square Feet | 59,638 |
| Project Completion Date | 4/23/2001 |
| CL&P Annual Energy Savings (kWh) | 139,950 |
| CL&P Lifetime Energy Savings (kWh) | 2,099,250 |
| Total Incentives | $28,810 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: | 8/29/2006 |
| Inspected By: | Peter McBride |

Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database

| Measure # | 1 | 1a |
| --- | --- | --- |
| Measure Description | Installation of monitoring equipment | Refrigeration re-commissioning |
| Measure Life (years) | 15 |  |
| Total Number of Units | 25 |  |
| CL&P-reported Annual kWh Savings | 139,950.00 | 0.00 |
| Assumptions in CL&P-reported Savings | (1) Annual savings with the monitoring system installation is estimated to be 5% of annual kWh consumption. (Eval audits shows 7% savings) |  |
| Calculation Methodology for CL&P-reported Savings |  |  |
| Inspection Action Items | 1) Ask energy savings methodology after installation of energy monitoring system. Show an example. 2) Ask is there any facility expansion, cutbacks after the completion of this project? What capacity if there are; and if they are all under monitoring system? 3) Collect Whole store annual utility bill for 2004 or other year after EEM. |  |
| Inspection Findings | Findings on the site visit on 8/29/2006: 1) Two Parasense monitoring panels have been installed to monitor kW, kWh, kVA and PF for racks A-E, A/C, lighting, bailer and compactors for this store. It also record indoor and outdoor temperatures and humidity. 2) The Parasense monitoring provider monitors the operation and downloads the data once a week. If there is (are) problem(s) identified, the provider report to the headquarters of this store. The management department will forward the report and inform technicians to fix the problems. According to the facility representative there was a period of time when the report could not be forwarded to technicians due to the organization issue. 3) The store has been expanded to 59,638 sq. ft from 43,132 sq. ft. since 2004. 4) There were one mechanical problem with valves and compressors identified by monitoring the Parasense system. 5) On site observations: - panels 230kW + 60 kW = 290 kW. Findings by the phone calls on 11/15/2006: 1) According to Steve Saunders from the store headquarters, the store has never connected the Parasense system even before the store remodel in 2004. | Findings on the site visit on 8/29/2006: 1) The store regularly tries new things to save energy utilizing the Parasense monitoring system. 2) The store has once monitored the racks refrigeration system power consumption through the Parasense system for 6 to 12 months. Based on the observations, the store optimized the rack temperature set points, and implemented the set points right after. 3) The rack compressors suction pressure has been raised to improve the refrigeration system operating efficiency. |

| Measure No. | Measure Description | Annual Hours | Annual Electricity Savings (kWh) | Lifetime (yrs) | Lifetime Electricity Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant | CL&P | Nexant |
| 1 | Installation of monitoring equipment |  | 0.00 |  | 0.00 |  | 0.00 |  | 0.00 | 0.00 | 0.00 |
| 1a | Refrigeration re-commissioning |  | 0.00 |  | 0.00 | 15 | 0.00 | 15 | 0.00 | 0.00 | 0.00 |
| Project level |  | 0.00 |  | 0.00 |  | 0.00 |  | 0.00 | 0.00 | 0.00 |
| Nexant Calculations: |  |  |  |  |  |  |  |  |  |  |
| EEM1#: | Nexant determined 0 kWh and 0 kW savings for this project since the Parasense system has never been put into function based on the store headquarters. |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-01-M-028 |
| Facility Type | Manufacturing |
| Building Square Feet |  |
| Project Completion Date | 12/7/2001 |
| Annual Energy Savings (kWh) | 73,039.00 |
| Lifetime Energy Savings (kWh) | 1,256,225.00 |
| Total Incentives | $4,161.12 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: |  |
| Inspected By: |  |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 | 3 |
| --- | --- | --- | --- |
| Measure Description | Repair compressed air leaks | Add a pony compressor system | Add cycling dryer with no-loss drain |
| Measure Life (years) | 5 | 20 | 15 |
| Total Number of Units |  | 1 | 1 |
| CL&P-reported kWh Savings | 7,343.00 | 46,814.00 | 18,882.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = 5 cfm (2) Rate 115 cfm (3) load requirement (including leakage): 45cfm@100psig 7:00am-4:00pm M-F 20cfm@100psig 4:00pm-7:00am M-F, SA, SUN (4) It is linear relation between cfm and kW. (5) full load M.E.= 0.9; No load M.E.=0.895 | (1) Pony compressor run 50% of load (2) Lights out hours: 6150hrs/year (3) It is linear relation between cfm and kW. (4) Pony compressor: 4.26 kW. | (1) Plant Air Load and Lights Out period are 2250 hrs and 6150 hrs respectively. (2) CFM demand during Plant Air Load and Lights Out period are 40 CFM and 15 CFM respectively. (3) It is linear between cfm% and kW% (4) 1/4" no-l loss drain (5) Coefficient 0.4 (6) Existing dryer power: 2.01kW; new dryer: 1.0kW |
| Calculation Methodology for CL&P-reported Savings | Before Leakage repair - After repair (compressor power + cooler fan power) BASE 4:00am-7:00pm: 2250hrsx((33 BHP/0.9x(45/115) + 8.25BHP/0.895x (1-45/115)+0.25BHP/0.85X 100%)x 0.746 7:00pm-4:00am M-SUN: 6150hrsx((33 BHP/0.9x(20/115) + 8.25BHP/0.895x (1-20/115)+0.25BHP/0.85X 100%)x 0.746 EEM 1# 4:00am-7:00pm: 2250hrsx((33 BHP/0.9x(40/115) + 8.25BHP/0.895x (1-40/115)+0.25BHP/0.85X 100%)x 0.746 7:00pm-4:00am M-SUN: 6150hrsx((33 BHP/0.9x(15/115) + 8.25BHP/0.895x (1-15/115)+0.25BHP/0.85X 100%)x 0.746 =59,914kWh kWh Savings = BASE- EEM 1# | Difference of total kWh before and after implementation of measure 2# BASE: (EEM 1# 7:00pm to 4:00am) = 59,914kWh EEM 2#: 4.26kW x 50% x 6150 = 13,000 kWh Savings = BASE - EEM 2# = 59,914kWh - 13,000 kWh = 46,814 kWh | (1) Savings with Dryer change: Plant Air Load: (2.01kW x100% x 2250hrs - 1.0 kW x (40cfm/125 cfm) x 2250hrs Lights Out Pd.: (2.01kW x100% x 6150hrs - 1.0kW x (15cfm/125 cfm) x 6150hrs (2) Savings due to no-loss drain in cycling dryer: 1/4" timed drain = 5sec/125 sec. x 104cfm x 0.4 coef. = 1.73cfm 5hp Comp savings = 4.26kW/16.4cfm x 1.73cfm x 6150 hrs = 2,764 kwh; 30 hp comp savings = (27.35kW loaded -6.87kWunloaded)/115cfm x 1.73cfm x 2250hrs= 693kWh; Total savings = (1) + (2) = 18,882 kWh |
| Inspection Action Items | 1) Were all 5 cfm leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What are the actual compressor full load/no load hours? 5) What is actual cfm demand for 7:00am-4:00pm and for 7:00pm-4:00am? 6) Check main compressor control method. 7) What is main compressor full load and no load kW? 8) Check how many leakage units? | 1) What is the actual cfm demand during "Lights Out" hours? 2) What are Lights Out hours for current and previous operation? 3) What is the name plate or capacity of main compressor? 4) Fill out New equipment information for EEM 2# 5) Verify the actual pony compressor kW. | 1) Verify that the new dryer and no loss drain are installed and operating? 2) Please verify real kW for non-cycling and cycling dryer? 3) Please verify the real % load for non-cycling dryer? 4) What is kW and cfm for 15hp pony compressor? 5) Verify old drain open 5 seconds every 2 minutes? 6) What is the kw/ton for no-cycling and cycling dryer under partial load? 7) Fill out the equipment information for the existing and new dryers. |
| Inspection Findings | 1. This facility is out of business based on the notice from Chris Saunders (NEU) on 8/15/2006. Nexant treats this project as a closed site. |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | CE-04-M-007 |
| Building Type | Manufacturing |
| Building Square Feet |  |
| Project Completion Date | 12/3/2004 |
| Annual Energy Savings (kWh) | 567,920.00 |
| Lifetime Energy Savings (kWh) | 6,164,400.00 |
| Total Incentives | $6,059.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: |  |
| Inspected By: |  |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Repair compressed air leaks | Re-gear compressor w/o VFD to the one w VFD |
| Measure Life (years) | 10 | 15 |
| Total Number of Units | 26 valves | Re-gear compressor |
| CL&P-reported kWh Savings | 470,880.00 | 97,040.00 |
| Assumptions in CL&P-reported Savings | (1) Leakage repaired = 204 CFM (2) Operating efficiency: 90% power at 85% CFM load. (3) Total planned leaking hours = 8000hrs | (1) Average plant CFM requirement = 400CFM. (2) Base line: Compressor 1# full operating (240cfm); Compressor 2#: 66% CFM load (160cfm); 66% power (3) EEM: Compressor 1# full operating (240cfm); Compressor 2#: 66% CFM load (160cfm); 48% power (4) Comp 1#, 2# : 82.5hp, Me. eff. = 94.1% |
| Calculation Methodology for CL&P-reported Savings | 1) 90% power with 85% cfm load: 90% x 82.5/0.941 x 0.746 x 90% = 58.86 kW 2) annual savings by repairing the tunnel and re-grind room: 8000 hrs x 58.86 = 470,880 kWh | (1) Baseline: Compressor 1#: 82.5/0.941 x 0.746 x 8000 = 532,200 kWh Compressor 2#: 82.5/0.941 x 0.746 x 66% x 8000 = 355,920 (2) EEM: Compressor 1#: 82.5/0.941 x 0.746 x 8000 = 532,200 kWh Compressor 2#: 82.5/0.941 x 0.746 x 48% x 8000 = 258,880 kWh (3) Savings: = (1) - (2) = 782,080 kWh |
| Inspection Action Items | 1) Were all leaks repaired? If not, where were repaired? Show repair list, or take sample to check if they were repaired and % of repair. (Valve leakage is just major leakage, not all) 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is the actual total hours with compressors on (is it 8000) 5) Collect CAC chart for compressor power operation data. 6) The airflow of leakage was measured? Measure current CFM at compressor discharge and production demand if possible? 7) Was leakage difference with and without production measured? | (1) Verify that this measure was actually implemented? (SSRXP75 was geared to SSREP75) (2) Check actual CFM load? How about baseline? (3) Check the current control method for each of the three compressors (corresponding to Equipment List table). (4) Check current VFD speed for the compressor with VFD control. (5) Check which compressors are running. |
| Inspection Findings | 1. This facility is out of business based on the notice from Chris Saunders (NEU) on 8/15/2006. Nexant treats this project as a closed site. |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-04-M-002 |
| Building Type | Manufacturing |
| Building Square Feet |  |
| Project Completion Date | 11/23/2004 |
| Annual Energy Savings (kWh) | 264,858.00 |
| Lifetime Energy Savings (kWh) | 2,648,580.00 |
| Total Incentives | $11,870.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: |  |
| Inspected By: |  |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 | 2 |
| --- | --- | --- |
| Measure Description | Repair compressed air leaks | No-Loss Drains |
| Measure Life (years) | 10 | 10 |
| Total Number of Units | 39 | 4 |
| CL&P-reported kWh Savings | 249,021.00 | 158,376.00 |
| Assumptions in CL&P-reported Savings | (1) leakage repaired = 107 CFM (2) BASE LINE Load and hours are distributed below: PEAK operation: 4992 hours (16hrs/day x 6 days/week x 52 weeks) 550 cfm 1#: 30% load and 51% power 2# and 3#: 100% load LOW DEMAND operation: 2496 hours (8hrs/day x 6 days/week x 52 weeks) 300 cfm 1#: 26% load and 49% power; 2#: 100% load; 3#: off SANITATION DAYS operation: 1272 hours (24hrs/day x 1 day/week x 52 weeks) 200 cfm 1#: 82% load and 84% power; 2# and 3#: off (3) EEM1#: Reduce air flow by 107cfm. PEAK operation: 443cfm 1#: 84% load and 86% power 2# : 100% load; 3#: off LOW DEMAND operation: 193cfm 1#: 79% load and 82% power; 2# and 3#: off SANITATION DAYS operation: 93cfm 1#: 38% load and 59% power; 2# and 3#: off | (1) Coefficient of Flow= 0.40 (2) Diameter of orifice (dia.) = 5/16 in (3) Total planned leaking hours = 8760 (4) Upstream pressure = 100.0 psig (5) Old drain has timing 10 seconds on and 3 minutes off? (6) EEM2#: Reduce air flow by 14cfm. PEAK operation: 429cfm 1#: 79% load and 82% power 2# : 100% load; 3#: off LOW DEMAND operation: 179cfm 1#: 74% load and 78% power; 2# and 3#: off SANITATION DAYS operation: 79cfm 1#: 33% load and 56% power; 2# and 3#: off |
| Calculation Methodology for CL&P-reported Savings | BASE LINE energy: (1) PEAK: (51% x 46.9kW + 46.9kW+ 47.6kW) x 4992hrs (2) LOW DEMAND: (49% x 46.9 +46.9kW) x 2496hrs (3) SANITARY: 84% x 46.9kW x 1272hrs EEM1# energy: (1) PEAK: (86% x 46.9kW + 1 x 46.9kW) x 4992hrs (2) LOW DEMAND: (82% x 46.9 ) x 2496hrs (3) SANITARY: 59% x 46.9kW x 1272hrs kWh savings = Base line - EEM 1# = 815682 -566661= 249,021 kW savings = (51%x46.9+46.9+47.6)-(86%x46.9+1x46.9) = 32.2 | 2 timer Drains: 5/16" orifice@100psig = 162cfm x 0.4 x 10 sec./190 sec. = 3.4 cfm/each 2 manual drains: measured to be 7cfm. Total 3.4x2 +7 = 14 cfm air can be reduced BASE LINE energy = EEM1# energy: EEM2# energy: (1) PEAK: (82% x 46.9kW + 1 x 46.9kW) x 4992hrs (2) LOW DEMAND: (78% x 46.9 ) x 2496hrs (3) SANITARY: 56% x 46.9kW x 1272hrs kWh savings = Base line - EEM 2# = 566,661-550,824 = 15,837 kW savings = (86%x46.9+1x46.9)-(82%x46.9+1x46.9)= 1.88 |
| Inspection Action Items | 1) Were all 39 (107cfm) leaks repaired? Show repair list, or take sample to check if they were repaired and % of repair. 2) Other leaks surveys performed? 3) Other leaks repairs performed? 4) What is actual CFM load in peak, low demand and sanitary? 5) Verify actual hours in peak, low demand and sanitary periods? 6) Verify if three compressors operate as in the calculation? 7) Collect compressor operation data sheet including power consumption at different CFM? 8) Verify that the compressors are operating and sequenced as the calculations assumed. 9) Check compressors control type to realize the load % assumption in the calculations. 10) Collect compressors nameplates | 1) Verify that the old drain diameter was 5/16"? 2) Check if old timer drains had timing 10 seconds on and 3 minutes off? 3) Inspect each drain to verify its existence. 4) What is actual drain pressure? 5) Check if the old manual drains always released air 7cfm? 6) Check if 4 drains have been placed? |
| Inspection Findings | 1. On 7/25, john hebeler, a consultant who once worked on projects for this facility, called Nexant and told Nexant that the production of this facility has moved to another state since 11/1/2005. Currently, this facility has become a distribution center and there is no longer any production taking place. All the compressors were sold between Sep and Oct 2005 and there has been no production there since then. Therefore, Nexant treats this project as a closed site. |

| Program Name | CL&P O&M Program |
| --- | --- |
| Project Number | WE-04-M-010 |
| Building Type | Office |
| Building Square Feet |  |
| Completion date | 11/18/2004 |
| Annual Energy Savings (kWh) | 171,696.00 |
| Lifetime Energy Savings (kWh) | 2,575,440.00 |
| Total Incentives | $24,520.00 |
| Nexant Reviewer | Yujie Cui @ 914-609-0388 |
| Inspection Date: |  |
| Inspected By: |  |
| Note: Annual and lifetime energy kWh savings are based on CL&P project documents and may differ from the program tracking database |

| Measure # | 1 |
| --- | --- |
| Measure Description | control system repair |
| Measure Life (years) | 15 |
| Total Number of Units | 3 |
| CL&P-reported kWh Savings | 183,495.00 |
| Assumptions in CL&P-reported Savings | (1) Space Information: Room Area People CFM LTG KW LOBBY 1000 6 1200 0.75 Back Lobby 1090 4 1900 1.2 SM CONF RM 320 8 600 0.956 LG CONF RM 620 20 1200 1.768 DEMO 1795 8 7200 2.016 CAFETERIA 542 40 2400 2 Total 5367 86 14500 8.69 (2) ENVELOPE U value: Glass = 0.5; Wall = 0.08; Roof = 0.08 (3) OCCUPIE HOURS: 50HRS/WEEK (4) Infiltration: 0.6 ACH (5) VAV minimum = 15% (6) Chiller eff. = 1.0 kW/ton (7) Boiler eff = 83% (8) Occupancy, lights and misc load diversity 100% (9) SF: 20hp; RF: 10hp |
| Calculation Methodology for CL&P-reported Savings | Used Tracer 700 (Trane Company) software with the input information as above |
| Inspection Action Items | 1) Ask what measures have been implemented? What operation has been changed? 2) What is AHU9 operating schedule? 3) How much % of conference is in the exterior zone? 4) Are lighting off when it is unoccupied? 5) How often the conference is used? 6) Ask for Chiller operation history before and after EEM? 7) VFDs trending data for supply and return fan? 8) Return fan speed control method? 9) Current static pressure set point? 10) Check current and before economizer operation? What is current supply air temperature reset? 11) What is Hp for boiler condensation pump and boiler fan? 12) Does boiler operate year around? 13) Are all boxes are VAV boxes? What type? What is minimum setting? 14) Chiller nameplate? What are HPs for CHW pump, cond. pump and tower fan? 15) Will chiller run when outside air temperature is below 35F? 16) Does hot water pump have VFD? 17) Collect AHU9 nameplate and rated data (including cfm, fan power and tonnage)? ----------------------------------------------------------------------- The problems in the input: 1) Too much cooling flow is assigned to each space. 2) After 7000 cfm OA is introduced, there is going to have cooling penalty in summer. 3) Occupancy diversity should not be 100%. 4) Chiller eff. may much higher than 1.0kw/ton. |
| Inspection Findings | 1. Nexant went to this site on 7/11/06, but found that this company has been gone since Dec 2005 based on the building guard. This facility is being filled by another company. Three or four maintenance people from this company were in the building for the facility transition. Nexant left CL&P cover letter and Nexant's request to inspect this facility along with Nexant contact information to the building security guard Joe, asking for his transfer to the facility manager. 2. Since Nexant has never been responded by the facility manager, this project was treated as no response. |

# Appendix 4: Survey Instrument

The following survey form was developed used by Nexant to collect data from each of the 34 inspected facilities.

Interviewer Name:	 ________________________________________

Date:			 ________________________________________

Respondent Name:	 ________________________________________

Organization:		 ________________________________________

Address:		 ________________________________________

City:			 ________________________________________

Tel:			 ________________________________________

Cell:			 ________________________________________

Email:			 ________________________________________

Introduction

Hello, my name is ______ from Nexant and I’m here for our appointment to talk about your facility and your participation in the Northeast Utilities Operations & Maintenance program.  These questions should last about 20 minutes.

First I have a few questions about your facility.

Firmographic characteristics

F1. Which of the following categories best describes this facility? [CIRCLE ONE]

- Retail

- Grocery

- Office/bank

- Restaurant/food service

- Warehouse

- Hospital

- Other health care

- Hotel/motel

- Automobile service

- Laboratory

- Library/museum

- Dormitory

- College/university—other building type

- Other school (e.g., K-12 or trade school)

- Multifamily housing

- Manufacturing

- Religious

- Government

- Social/amusement

- Other?  [SPECIFY] ________________

F2. How many buildings are located in this facility?

Number of buildings _____

F3. What is the approximate square footage of the/each building? (in square feet)

Building 1  Sq. ft. ________________

Building 2  Sq. ft. ________________

Building 3  Sq. ft. ________________

Building 4  Sq. ft. ________________

F4.  In which spaces were program measures implemented (E.G, PROCESS, REFRIGERATION, WAREHOUSE, OFFICE, KITCHEN, SHOWROOM, ETC.)?

Number of Employees

O1. Before participating in the O&M program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION], how many full-time equivalent (FTE) employees worked at this facility?

Year round (average) ______

O2a. Before participating, did the number of FTE employees vary throughout the year?   [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #O3a]

3. Don’t Know		[SKIP TO #O3a]

O2b. [IF YES] What was the number of FTE employees by month in the year preceding [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?

J____ F____ M____ A____ M____ J____ J____ A____ S____ O____ N____ D____

O3a. Have the number of FTE employees changed since participating in the program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?   [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #O4]

3. Don’t Know		[SKIP TO #O4]

O3b. [IF YES] How many full-time equivalent employees currently work at this facility?

Year round (average) ______

O3c. Since participating in the program, does the number of FTE employees vary throughout the year?   [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #O4]

3. Don’t Know		[SKIP TO #O4]

O3d. [IF YES] What is the number of FTE employees by month in the year since [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?

J____ F____ M____ A____ M____ J____ J____ A____ S____ O____ N____ D____

Pre-program Operating Characteristics

From now on, I would like you to answer questions ONLY for the spaces where program measures were implemented.

O4. Before program participation, what was the schedule at full capacity in the spaces where program measures were implemented? [USE 24-HOUR CLOCK]

CHECK HERE IF 24/7 _____ [SKIP TO #O5]

M _____:_____	to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

W _____:_____to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

F _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

O5. During which months was the facility at full capacity before participation?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D    Year-round [SKIP TO #08a]

O6. Before program participation, what was the schedule at partial capacity in the spaces where program measures were implemented? [USE 24-HOUR CLOCK]

CHECK HERE IF ALWAYS AT FULL CAPACITY  _____ [SKIP TO #O8]

M _____:_____	to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

W _____:_____to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

F _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

O7a. [IF PARTIAL CAPACITY] During which months was the facility at partial capacity?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D   Year-round

O7b. [IF PARTIAL CAPACITY] What percent of full capacity would you consider partial capacity to be? (E.G. 50%, 75%, etc]

_________%

O8a. Prior to participating in the program, how many days per year did scheduled shut downs occur in the spaces where program measures were implemented?

ENTER AVERAGE # DAYS ______

O8b. [IF #O8a >0] During which months did scheduled shutdowns occur?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D

O9a. How many days per year did unscheduled shut downs occur in the spaces where program measures were implemented?

ENTER AVERAGE # DAYS ______

O9b. [IF #O9a >0] During which months did unscheduled shutdowns occur?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D

Post-Program Operating Characteristics

O10. Have the hours of operation changed since participating in the program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?  [CIRCLE ONE]

1. Yes

2. No 		[SKIP TO #O15a]

3. Don’t Know		[SKIP TO #O15a]

O11. What is the current schedule at full capacity in the spaces where program measures were implemented? [USE 24-HOUR CLOCK]

CHECK HERE IF 24/7 _____ [SKIP TO #O12]

M _____:_____	to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

W _____:_____to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

F _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

O12. Currently, during which months is the facility at full capacity?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D   Year-round [SKIP TO #015a]

O13. What is the current schedule at partial capacity in the spaces where program measures were implemented? [USE 24-HOUR CLOCK]

CHECK HERE IF ALWAYS AT FULL CAPACITY  _____ [SKIP TO #O15a]

M _____:_____	to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

W _____:_____to _____:_____  	OR 24 hours ____

T _____:_____ 	to _____:_____  	OR 24 hours ____

F _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

S _____:_____ 	to _____:_____  	OR 24 hours ____

O14a. [IF PARTIAL CAPACITY] Currently during which months is the facility at partial capacity?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D   Year-round

O14b. [IF PARTIAL CAPACITY] What percent of full capacity would you consider partial capacity to be? (E.G. 50%, 75%, etc]

_________%

O15a. How many days per year do scheduled shut downs occur since participating in the program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?

ENTER AVERAGE # DAYS ______

O15b. [IF O15a >0] During which months did the scheduled shutdowns occur?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D

O16a. How many days per year do unscheduled shut downs occur since participating in the program?

ENTER AVERAGE # DAYS ______

O16b. [IF O16a >0] During which months did unscheduled shutdowns occur?

[CIRCLE]   J   F   M   A   M   J    J   A   S   O   N   D

O17. Is the current level of production at this facility higher, lower, or about the same as it was before program participation? [CIRCLE ONE]

1. Higher

2. Lower

3. Same		[SKIP TO #V1]

4. Don’t Know		[SKIP TO #V1]

O18.  [IF HIGHER OR LOWER] In percentage terms, what is the approximate production level now compared to before program participation?  [E.G., IF PRODUCTION IS NOW 20% HIGHER, RECORD 120%; IF PRODUCTION IS NOW 20% LOWER, RECORD 80%]

_________%

Verification of Program Recommendations

Here is a list of recommendations from the program audit. [HAND LIST OF RECOMMENDATIONS TO THE RESPONDENT]

V1. Which program recommendations were fully implemented, partially implemented, or not implemented at all?   [RECORD RESPONSES FOR QUESTIONS V1-V4 ON RECOMMENDATIONS LIST]

1. Fully Implemented		[SKIP TO #V3]

2. Partially Implemented

3. Not Implemented		[SKIP TO #V3]

4. Don’t Know			[SKIP TO #V3]

V2. [IF RECOMMENDATION PARTIALLY IMPLEMENTED] Describe any deviations from the recommendation.

V3. Are the equipment and controls still functioning as intended?  [CIRCLE ONE]

1. Yes			[SKIP TO #V5]

2. No

3. Don’t Know		[SKIP TO #V5]

V4. [IF NO] Why isn’t the equipment functioning as intended?

V5. Are there any other measures you have installed or changes in operations and maintenance you have made because of this program?  [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #M1]

3. Don’t Know		[SKIP TO #M1]

V6. [IF YES] What other measures or changes have you implemented?

V7. [IF YES] Can you estimate the electric savings, in percent, that have resulted from these measures or changes?

Maintenance schedules

M1. Have the maintenance schedules changed since participating in the program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION]?  [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #M3]

3. Don’t Know		[SKIP TO #M3]

M2. Before participating in the program in [INSERT MONTH/YEAR OF PROGRAM PARTICIPATION], how many times per year did the following equipment receive scheduled maintenance?

READ LIST OF EQUIPMENT IMPACTED BY RECOMMENDATIONS & RECORD NUMBER OF TIMES PER YEAR

M3. Since participating in the program, how many times per year does the following equipment receive scheduled maintenance?

READ LIST OF EQUIPMENT IMPACTED BY RECOMMENDATIONS & RECORD NUMBER OF TIMES PER YEAR

Equipment & Controls

E1. Since participating in the program, have there been any other major equipment changes to the facility beyond those recommended by the program?  [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #E3]

3. Don’t Know		[SKIP TO #E3]

E2. Please describe these equipment changes.

E3. Since participating in the program, have there been any other changes to control systems beyond those recommended by the program?  [CIRCLE ONE]

1. Yes

2. No 			[SKIP TO #NE1]

3. Don’t Know		[SKIP TO #NE1]

E4. Please describe these changes to the control systems. [Prompt timers, monitoring systems, EMS, motion detectors, etc]

Non-Electricity Impacts

NE1. What does staff say about their experiences with the measures and O&M changes introduced through the program? Do they mention any non-electricity costs or benefits?  [PROBE THE FOLLOWING ITEMS, CHECK OFF IF A POSITIVE RESPONSE]

1. Changes in productivity				_____

2. Changes in sick time					_____

3. Changes in safety					_____

4. Changes in employee morale				_____

5. Changes in sales					_____

6. Changes in maintenance costs				_____

7. Changes in maintenance labor				_____

8. Changes in consumption of other fuels		_____

9. Changes in consumption of water			_____

10. Changes in the environmental impact of the facility	_____

11. Any Others? ____________________		_____

12. Any Others? ____________________		_____

13. Any Others?_____________________		_____

14. Any Others?_____________________		_____

15. Any Others?_____________________		_____

NE2. We estimate that the annual electricity cost savings from the program recommendations that you implemented will be worth approximately [$X,XXX—NEXANT INSERT].  In dollar terms, please provide your own estimate of the minimum annual electricity cost savings stemming from your participation in the program, the maximum, and the figure you consider most likely.

Minimum: 	$_________

Maximum: 	$_________

Likely:		$_________

NE3. Now I’m going to read you a list of possible effects other than electricity savings that may have occurred because of the recommendations made through this program, and I’d like you to tell me how much each effect is worth, as a percentage of the likely electricity savings figure we were just discussing.  Also, please tell me if the effect is positive, and saves money, or is negative, and costs your facility money.

| Non-electricity Impact | % compared to likely electricity savings | Pos or Neg | Rank |
| --- | --- | --- | --- |
| Changes in productivity | ___________% | Pos Neg |  |
| Changes in sick time | ___________% | Pos Neg |  |
| Changes in safety | ___________% | Pos Neg |  |
| Changes in employee morale | ___________% | Pos Neg |  |
| Changes in sales | ___________% | Pos Neg |  |
| Changes in maintenance costs | ___________% | Pos Neg |  |
| Changes in maintenance labor | ___________% | Pos Neg |  |
| Changes in consumption of other fuels | ___________% | Pos Neg |  |
| Changes in consumption of water | ___________% | Pos Neg |  |
| Changes in the environmental impact of the facility | ___________% | Pos Neg |  |
| Others _____________________ ___________________________ | ___________% | Pos Neg |  |
| Others _____________________ ___________________________ | ___________% | Pos Neg |  |
| Others _____________________ ___________________________ | ___________% | Pos Neg |  |
| Others _____________________ ___________________________ | ___________% | Pos Neg |  |
| Others _____________________ ___________________________ | ___________% | Pos Neg |  |

NE4. Please rank order these non-electricity effects from most positive to least positive for your facility.  [SHOW RESPONDENT THE ABOVE NEI LIST (SEPARATE SHEET) AND HAVE HIM/HER RANK THE ITEMS]

NE5. Overall, do you think the non-electricity effects of the measures installed and O&M changes made through this program are positive or negative?  [CIRCLE ONE]

1. Positive

2. Negative 		[SKIP TO #NE7]

3. Don’t Know		[END]

NE6. [IF POSITIVE] Please estimate in dollars how much all the non-electricity effects of these measures and O&M changes save the facility annually.

$___________

[SKIP TO END]

NE7. [IF NEGATIVE] Please estimate in dollars how much all the non-electricity effects of these measures and O&M changes cost the facility annually.

$____________

Thank you for your time and cooperation.

# Footnotes

Improving Compressed Air System Performance-a source book for industry